## Cover
SPECIFICATION FOR APPROVAL
Customer : | Insyde
Description : | UART Protocol for BMC application
Auras Model No. : | -
REV. | Date | Author | Status
1.00 | 2024-12-13 | Charles | Draft
1.01 | 2024-12-18 | Wendy | Add Sheet "Config整合"
1.02 | 2024-12-14 | Charles | 1. Modify "Minimum Transmission Time", B or H -> C 50ms 2. Modify "Error Event", Leakage Error Code 3. Add "Error Event", PSU Error Code 4. Modify "CDU Auto / Manual Mode Set", Target Flow byte nums
1.03 | 2025-01-13 | Charles | 1. Add "Set Configuration", 0xE0~0xE3,0xEF
1.04 | 2025-01-24 | Charles | 1. Modify "Error Event", Pump Error Code 2. Add "Error Event", PT-100 Eror Code 3. Modify "Error Event", FAN Row/Group Error Code 4. Modify "Error Event", PSU Error Code 5. Modify "FAN Door Info."
1.05 | 2025-02-08 | Charles | 1. Add "Set Configuration", 0xE4,0xEE
1.06 | 2025-02-24 | Charles | 1. Add "CDU Target Command Information"
1.07 | 2025-03-05 | Wendy | 1. Add Redfish Name 2. Add Web control Name
1.08 | 2025-03-06 | Wendy | 1. Revise Level Sensors state 2. Add fix Max & Min value
1.09 | 2025-03-18 | Wendy | 1. Revise Max Value以及Min Value
1.10 | 2025-03-20 | Wendy | 1. ADD Asking frequency
1.11 | 2025-03-26 | Wendy | 1. Modify the flow unit 2. Modify the Alarm_max setting, the lower limit of the flow rate, and the unit 3. Modify the lower limit value of MCU 4. Add DP
1.12 | 2025-04-01 | Wendy | 1. Added BMC IP Address Information 2.CDU Serial Number Information 3. Modify the flow, Pressure, Air_Velocity unit
1.13 | 2025-04-10 | Wendy | 1. Modify pressure, flow and FAN Door Information item of the Redfish Name page 2. Pumps Information ,RPM item of the Redfish Name page and Application Command ID page
1.14 | 2025-04-11 | Wedny | Added New requirements for solution A page
1.15 | 2025-04-17 | Wendy | 1.Modify Fan RPM 2. Added Remark for solution A page 3. Modify Application_Command_ID
1.16 | 2025-04-25 | Wendy | 1.Modify CDU Auto / Manual Mode Set for Application_Command_ID page 2. Modify Max Value and Alarm_max for Redfish_Name 3. Modify New requirements for solution A page

## Application Definition
UART Main Features of Auras BMC Protocol
Physical Layer
Symbol | Value
Baud Rate | 115200
Parity Bit | None
Data Bit | 8
Stop Bit | 1
Basic Frame
Byte Size | 1 | 1 | 1 | 1 | n | 1
Data | SOF | Source ID | Target ID | Length of Payload | Payload | Checksum
SOF | 0xAA
Source / Target ID | ID Symbol | Description
| B | BMC (Baseboard Management Controller)
| C | CDU (Cooling Distribution Unit)
| F | FD (Fan Door)
| T | DT (Diagnostic Tool)
Length of Payload / Payload | ex.
| Byte Size | Length of Payload: 1 | Payload: n = 3
| Data | 0x03 | 0x1D 0x34 0x9A
Checksum | Source ID + Target ID + Length of Payload + Payload 1+ Payload 2 + … + Payload n
Minimum Transmission Time
Source ID | Target ID | Transmission Time
B | C | 50 ms
H | C | 50 ms
C | F | 200 ms
H | F | 200 ms
ID Index Definition
Sort | Command ID Range
Common | 0xF0 ~ 0xFF
Peripheral Sensors | 0x10 ~ 0x1F
Setting Mode | 0x01 ~ 0x0F
Error Event | 0x20 ~ 0x2F

## Application_Command_ID
Application Command ID
|  | < Request > |  |  |  | < Reply >
1 | Common
| Query (0xF1) | BMC IP Address Information
|  | Any Device: |  |  |  | Any Device:
|  | Byte Index | Content | Comment |  | Byte Index | Content | Comment
|  | 0 | Command ID | As title |  | 0 | Command ID | As title
|  | 1 | Ethernet Port 1 Address #1 | XXX.XXX.XXX.XXX
|  | 2 | Ethernet Port 1 Address #2
|  | 3 | Ethernet Port 1 Address #3
|  | 4 | Ethernet Port 1 Address #4
|  | 5 | Ethernet Port 2 Address #1
|  | 6 | Ethernet Port 2 Address #2
|  | 7 | Ethernet Port 2 Address #3
|  | 8 | Ethernet Port 2 Address #4
| Query (0xF2) | CDU Serial Number Information
|  | Any Device: |  |  |  | Any Device:
|  | Byte Index | Content | Comment |  | Byte Index | Content | Comment
|  | 0 | Command ID | As title |  | 0 | Command ID | As title
|  | 1 | Component ID | C' = CDU 'F' = FD |  | 1 | Serial Number Byte#1 | ASCII
[6 empty] | 2 | Serial Number Byte#2
[6 empty] | 3 | Serial Number Byte#3
[6 empty] | 4 | Serial Number Byte#4
[6 empty] | 5 | Serial Number Byte#5
[6 empty] | 6 | Serial Number Byte#6
[6 empty] | 7 | Serial Number Byte#7
[6 empty] | 8 | Serial Number Byte#8
[6 empty] | 9 | Serial Number Byte#9
[6 empty] | 10 | Serial Number Byte#10
[6 empty] | 11 | Serial Number Byte#11
[6 empty] | 12 | Serial Number Byte#12
[6 empty] | 13 | Serial Number Byte#13
| Query (0xF3) | Firmware Version Information
|  | Any Device: |  |  |  | Any Device:
|  | Byte Index | Content | Comment |  | Byte Index | Content | Comment
|  | 0 | Command ID | As title |  | 0 | Command ID | As title
|  | 1 | Component ID | C' = CDU 'F' = FD |  | 1 | Application Version
[6 empty] | 2 | Application Reversion
[6 empty] | 3 | Bootloader Version
[6 empty] | 4 | Bootloader Reversion
2 | Peripheral Sensors
| Query (0x10) | Pressure Sensors Information
|  | Host: |  |  |  | CDU:
|  | Byte Index | Content | Comment |  | Byte Index | Content | Comment | Remark
|  | 0 | Command ID | As title |  | 0 | Command ID | As title | Unit: 0.01 kPa Format: uint16 Range: 0 ~65535
[6 empty] | 1 | Return Pressure 1 | LSB
[6 empty] | 2 |  | HSB
[6 empty] | 3 | Supply Pressure 2 | LSB
[6 empty] | 4 |  | HSB
[6 empty] | 5 | Primary Inlet Pressure 3 | LSB
[6 empty] | 6 |  | HSB
[6 empty] | 7 | Primary Outlet Pressure 4 | LSB
[6 empty] | 8 |  | HSB
| Query (0x11) | Temperature Sensors Information
|  | Host: |  |  |  | CDU:
|  | Byte Index | Content | Comment |  | Byte Index | Content | Comment | Remark
|  | 0 | Command ID | As title |  | 0 | Command ID | As title | Unit: 0.01 °C Format: int16
[6 empty] | 1 | MCU Temperature | LSB | Range: -2500 ~ 10000
[6 empty] | 2 |  | HSB
[6 empty] | 3 | PT-100 Temperature 1 | LSB | Range: -4000 ~ 12500
[6 empty] | 4 |  | HSB
[6 empty] | 5 | PT-100 Temperature 2 | LSB
[6 empty] | 6 |  | HSB
[6 empty] | 7 | PT-100 Temperature 3 | LSB
[6 empty] | 8 |  | HSB
[6 empty] | 9 | PT-100 Temperature 4 | LSB
[6 empty] | 10 |  | HSB
[6 empty] | 11 | Supply Flow Temperature 1 | LSB | Range: -2500 ~ 15000
[6 empty] | 12 |  | HSB
[6 empty] | 13 | Primary Outlet Flow Temperature 2 | LSB
[6 empty] | 14 |  | HSB
| Query (0x12) | Flow Sensors Information
|  | Host: |  |  |  | CDU:
|  | Byte Index | Content | Comment |  | Byte Index | Content | Comment | Remark
|  | 0 | Command ID | As title |  | 0 | Command ID | As title | Unit: 0.01 L/s Format: uint16 Range: 0 ~ 300
[6 empty] | 1 | Supply Flow 1 | LSB
[6 empty] | 2 |  | HSB
[6 empty] | 3 | Primary Outlet Flow 2 | LSB
[6 empty] | 4 |  | HSB
| Query (0x13) | Valve Gate Information
|  | Host: |  |  |  | CDU:
|  | Byte Index | Content | Comment |  | Byte Index | Content | Comment | Remark
|  | 0 | Command ID | As title |  | 0 | Command ID | As title | Unit: % Format: uint8 Range: 0 ~ 100
[6 empty] | 1 | Valve Gate
| Query (0x14) | Leakage Sensors State Information
|  | Host: |  |  |  | CDU: |  |  |  | Leakage State Table
|  | Byte Index | Content | Comment |  | Byte Index | Content | Comment | Remark | Bit Index | Content | Comment
|  | 0 | Command ID | As title |  | 0 | Command ID | As title | Unit: - Format: uint8 Range: 0 ~ 5 | 0 | State | 0: Disable 1: Normal 2: Leaking 3: Recovery 4: Alarm 5: Disconnect
[6 empty] | 1 | Leakage Detect Port 1 | see Table beside |  | 1
[6 empty] | 2 | Leakage Detect Port 2 |  |  | 2
[6 empty] | 3 | Leakage Detect Port 3 |  |  | 3
[6 empty] | 4 | Leakage Detect Port 4 |  |  | 4
[6 empty] | 5 | Leakage Detect Port 5 |  |  | 5
[6 empty] | 6 | Leakage Detect Port 6 |  |  | 6
7
| Query (0x15) | Leakage Sensors ADC Value
|  | Host: |  |  |  | CDU:
|  | Byte Index | Content | Comment |  | Byte Index | Content | Comment | Remark
|  | 0 | Command ID | As title |  | 0 | Command ID | As title | Unit: - Format: uint16 Range: 0 ~ 1023
[6 empty] | 1 | Leakage Detect Port 1 | LSB
[6 empty] | 2 |  | HSB
[6 empty] | 3 | Leakage Detect Port 2 | LSB
[6 empty] | 4 |  | HSB
[6 empty] | 5 | Leakage Detect Port 3 | LSB
[6 empty] | 6 |  | HSB
[6 empty] | 7 | Leakage Detect Port 4 | LSB
[6 empty] | 8 |  | HSB
[6 empty] | 9 | Leakage Detect Port 5 | LSB
[6 empty] | 10 |  | HSB
[6 empty] | 11 | Leakage Detect Port 6 | LSB
[6 empty] | 12 |  | HSB
| Query (0x16) | Level Sensors Information
|  | Host: |  |  |  | CDU: |  |  |  | Level Trigger Byte
|  | Byte Index | Content | Comment |  | Byte Index | Content | Comment | Remark | Bit Index | Content | Comment
|  | 0 | Command ID | As title |  | 0 | Command ID | As title | Unit: - Format: uint8 Range: 0x00 ~ 0xFF | 0 | Level 1 Trigger | 1: Yes 0: No
[6 empty] | 1 | Level Trigger Byte | see Table beside |  | 1 | Level 2 Trigger
2
3
4
5
6
7
| Query (0x17) | Pump LEDs Information
|  | Host: |  |  |  | CDU: |  |  |  | LED State Byte
|  | Byte Index | Content | Comment |  | Byte Index | Content | Comment | Remark | Bit Index | Content | Comment
|  | 0 | Command ID | As title |  | 0 | Command ID | As title | Unit: - Format: uint8 Range: 0x00 ~ 0xFF | 0 | LED_RED 1 | 0: On 1: Off
[6 empty] | 1 | LED State Byte | see Table beside |  | 1 | LED_RED 2
[10 empty] | 2 | LED_RED 3
[10 empty] | 3 | LED_GREEN 1
[6 empty] | 0 |  |  |  | 4 | LED_GREEN 2
[10 empty] | 5 | LED_GREEN 3
6
7
| Query (0x18) | Pumps Information
|  | Host: |  |  |  | CDU:
|  | Byte Index | Content | Comment |  | Byte Index | Content | Comment | Remark
|  | 0 | Command ID | As title |  | 0 | Command ID | As title | <PWM> Unit: % Format: uint8 Range: 0 ~ 100 <Speed> Unit: RPM Format: uint32 Range: 0 ~ 9000
[6 empty] | 1 | Pump 1 PWM
[6 empty] | 2 | Pump 1 Speed | LSB
[6 empty] | 3 |  | HSB
[6 empty] | 4 |  | USB
[6 empty] | 5 |  | MSB
[6 empty] | 6 | Pump 2 PWM
[6 empty] | 7 | Pump 2 Speed | LSB
[6 empty] | 8 |  | HSB
[6 empty] | 9 |  | USB
[6 empty] | 10 |  | MSB
[6 empty] | 11 | Pump 3 PWM
[6 empty] | 12 | Pump 3 Speed | LSB
[6 empty] | 13 |  | HSB
[6 empty] | 14 |  | USB
[6 empty] | 15 |  | MSB
| Query (0x19) | FAN Row A / B Information
|  | Host: |  |  |  | CDU:
|  | Byte Index | Content | Comment |  | Byte Index | Content | Comment | Remark
|  | 0 | Command ID | As title |  | 0 | Command ID | As title | <PWM> Unit: % Format: uint8 Range: 0 ~ 100 <Speed> Unit: RPM Format: uint32 Range: 0 ~ 20000
[6 empty] | 1 | FAN Row A PWM
[6 empty] | 2 | FAN Row A Speed 1 | LSB
[6 empty] | 3 |  | HSB
[6 empty] | 4 |  | USB
[6 empty] | 5 |  | MSB
[6 empty] | 6 | FAN Row A Speed 2 | LSB
[6 empty] | 7 |  | HSB
[6 empty] | 8 |  | USB
[6 empty] | 9 |  | MSB
[6 empty] | 10 | FAN Row A Speed 3 | LSB
[6 empty] | 11 |  | HSB
[6 empty] | 12 |  | USB
[6 empty] | 13 |  | MSB
[6 empty] | 14 | FAN Row A Speed 4 | LSB
[6 empty] | 15 |  | HSB
[6 empty] | 16 |  | USB
[6 empty] | 17 |  | MSB
[6 empty] | 18 | FAN Row A Speed 5 | LSB
[6 empty] | 19 |  | HSB
[6 empty] | 20 |  | USB
[6 empty] | 21 |  | MSB
[6 empty] | 22 | FAN Row B PWM
[6 empty] | 23 | FAN Row B Speed 1 | LSB
[6 empty] | 24 |  | HSB
[6 empty] | 25 |  | USB
[6 empty] | 26 |  | MSB
[6 empty] | 27 | FAN Row B Speed 2 | LSB
[6 empty] | 28 |  | HSB
[6 empty] | 29 |  | USB
[6 empty] | 30 |  | MSB
[6 empty] | 31 | FAN Row B Speed 3 | LSB
[6 empty] | 32 |  | HSB
[6 empty] | 33 |  | USB
[6 empty] | 34 |  | MSB
[6 empty] | 35 | FAN Row B Speed 4 | LSB
[6 empty] | 36 |  | HSB
[6 empty] | 37 |  | USB
[6 empty] | 38 |  | MSB
[6 empty] | 39 | FAN Row B Speed 5 | LSB
[6 empty] | 40 |  | HSB
[6 empty] | 41 |  | USB
[6 empty] | 42 |  | MSB
| Query (0x1A) | PSUs Information
|  | Host: |  |  |  | CDU:
|  | Byte Index | Content | Comment |  | Byte Index | Content | Comment | Remark
|  | 0 | Command ID | As title |  | 0 | Command ID | As title | <Power> Unit: 0.1W Format: uint16 Range: 0 ~ 13000 <Voltage> Unit: 0.1 V Format: uint16 Range: 0 ~ 512 <Current> Unit: 0.1 A Format: uint16 Range: 0 ~ 256
[6 empty] | 1 | PSU 1 Output Power | LSB
[6 empty] | 2 |  | HSB
[6 empty] | 3 | PSU 1 Output Voltage | LSB
[6 empty] | 4 |  | HSB
[6 empty] | 5 | PSU 1 Output Current | LSB
[6 empty] | 6 |  | HSB
[6 empty] | 7 | PSU 2 Output Power | LSB
[6 empty] | 8 |  | HSB
[6 empty] | 9 | PSU 2 Output Voltage | LSB
[6 empty] | 10 |  | HSB
[6 empty] | 11 | PSU 2 Output Current | LSB
[6 empty] | 12 |  | HSB
[6 empty] | 13 | PSU 3 Output Power | LSB
[6 empty] | 14 |  | HSB
[6 empty] | 15 | PSU 3 Output Voltage | LSB
[6 empty] | 16 |  | HSB
[6 empty] | 17 | PSU 3 Output Current | LSB
[6 empty] | 18 |  | HSB
| Query (0x1B) | FAN Door Information
|  | Any Device: |  |  |  | Any Device:
|  | Byte Index | Content | Comment |  | Byte Index | Content | Comment | Remark
|  | 0 | Command ID | As title |  | 0 | Command ID | As title
|  | 1 | Component #n | 0 = Group 0 1 = Group 1 2 = Group 2 3 = Group 3 4 = Group 4 |  | 1 | FAN Group #n PWM |  | <PWM> Unit: % Format: uint8 Range: 0 ~ 100
[6 empty] | 2 | FAN Group #n Speed 1 | LSB | <Speed> Unit: RPM Format: uint32 Range: 0 ~ 8000
[6 empty] | 3 |  | HSB
[6 empty] | 4 |  | USB
[6 empty] | 5 |  | MSB
[6 empty] | 6 | FAN Group #n Speed 2 | LSB
[6 empty] | 7 |  | HSB
[6 empty] | 8 |  | USB
[6 empty] | 9 |  | MSB
[6 empty] | 10 | FAN Group #n Speed 3 | LSB
[6 empty] | 11 |  | HSB
[6 empty] | 12 |  | USB
[6 empty] | 13 |  | MSB
[6 empty] | 14 | FAN Group #n Speed 4 | LSB
[6 empty] | 15 |  | HSB
[6 empty] | 16 |  | USB
[6 empty] | 17 |  | MSB
[6 empty] | 18 | FAN Group #n Current 1 | LSB | Unit: 0.1 A Format: uint16 Range: 0 ~ 256
[6 empty] | 19 |  | HSB
[6 empty] | 20 | FAN Group #n Current 2 | LSB
[6 empty] | 21 |  | HSB
[6 empty] | 22 | FAN Group #n Current 3 | LSB
[6 empty] | 23 |  | HSB
[6 empty] | 24 | FAN Group #n Current 4 | LSB
[6 empty] | 25 |  | HSB
[6 empty] | 26 | FAN Group #n Air Inlet Flow | LSB | Unit: 0.01 CFM Format: uint16 Range: 0 ~ 30000
[6 empty] | 27 |  | HSB
[6 empty] | 28 | FAN Group #n Air Inlet Temperature | LSB | Unit: 0.01 °C Format: int16 Range: –12800 ~ 12800
[6 empty] | 29 |  | HSB
[6 empty] | 30 | FAN Group #n Air Ouletlet Temperature | LSB
[6 empty] | 31 |  | HSB
3 | Setting Mode
| Modify (0x01) | CDU Auto / Manual Mode Set
|  | Host: |  |  |  | CDU:
|  | Byte Index | Content | Comment | Remark | Byte Index | Content | Comment
|  | 0 | Command ID | As title |  | 0 | Command ID | As title
|  | 1 | Set Mode | 0, 1 = Auto 2, 3, 4 = Auto + Manual 255 = Manual | 0 = TMP + PSR Auto Mode -> byte index 2 + 3 1 = TMP + Flow Auto Mode -> byte index 2 + 4~5 2 = TMP Auto + Pump PWM Manual -> byte index 2 + 7~9 3 = PSR Auto + Valve/FAN PWM Manual -> byte index 3 + 6 / 10~11 / 12~16 4 = Flow Auto + Valve/FAN PWM Manual -> byte index 4~5 + 6 / 10~11 / 12~16 255 = Manual Mode -> byte index 6~16 < Target Range > <Temperature> Unit: 0.1(°C) Format: uint16 Range: 0 ~ 800 <Pressure> Unit: 0.1(kPa) Format: uint16 Range: 0 ~ 6000 <Flow> Unit: 0.1(L/s) Format: uint 8 Range: 0 ~ 80 | 1 | Set Mode | 0, 1 = Auto 2, 3, 4 = Auto + Manual 255 = Manual
|  | 2 | Target Temperature | LSB
|  | 3 |  | HSB
|  | 4 | Target Pressure | LSB
|  | 5 |  | HSB
|  | 6 | Target Flow |  |  |  | cdustm32io-tools -t 11 n 1 0 0 0 0 0 50 50 50 0 0 0 0 0 0 0
|  | 7 | Valve Gate | 0 ~ 100 (%)
|  | 8 | Pump 1 PWM
|  | 9 | Pump 2 PWM
|  | 10 | Pump 3 PWM
|  | 11 | FAN Row A PWM
|  | 12 | FAN Row B PWM
|  | 13 | FAN Group 0 PWM | 0 ~ 100 (%)
|  | 14 | FAN Group 1 PWM
|  | 15 | FAN Group 2 PWM
|  | 16 | FAN Group 3 PWM
|  | 17 | FAN Group 4 PWM
| Query (0x02) | CDU Target Command Information
|  | Host: |  |  |  | CDU:
|  | Byte Index | Content | Comment | Remark | Byte Index | Content | Comment
|  | 0 | Command ID | As title |  | 0 | Command ID | As title
[6 empty] | 1 | Set Mode | 0, 1 = Auto 2, 3, 4 = Auto + Manual 255 = Manual
[6 empty] | 2 | Target Temperature | LSB
[6 empty] | 3 |  | HSB
[6 empty] | 4 | Target Pressure | LSB
[6 empty] | 5 |  | HSB
[6 empty] | 6 | Target Flow
| Modify (0x03) | FAN Door Auto / Manual Mode Set
|  | CDU: |  |  |  | Fan Door:
|  | Byte Index | Content | Comment | Remark | Byte Index | Content | Comment
|  | 0 | Command ID | As title |  | 0 | Command ID | As title
|  | 1 | FAN Group 0 PWM | 0 ~ 100 (%) | Auto / Manual Mode Active | 1 | Set Mode | 0 = Auto Mode 1 = Manual Mode
|  | 2 | FAN Group 1 PWM
|  | 3 | FAN Group 2 PWM
|  | 4 | FAN Group 3 PWM
|  | 5 | FAN Group 4 PWM
4 | Error Event
| Query (0x20) | Error Event Information
|  | Host: |  |  |  | CDU: |  |  |  | Leakage Error Code Byte
|  | Byte Index | Content | Comment |  | Byte Index | Content | Comment |  | Bit Index | Content | Comment
|  | 0 | Command ID | As title |  | 0 | Command ID | As title |  | 0 | Leakage Port 1 | 0: Normal 1: Alarm
[6 empty] | 1 | Return Pressure 1 Error Code | 0 = No Error 1 = Out of Pressure 2 = Over Pressure 3 = Under Pressure |  | 1 | Leakage Port 2
[6 empty] | 2 | Supply Pressure 2 Error Code |  |  | 2 | Leakage Port 3
[6 empty] | 3 | Primary Inlet Pressure 3 Error Code |  |  | 3 | Leakage Port 4
[6 empty] | 4 | Primary Outlet Pressure 4 Error Code |  |  | 4 | Leakage Port 5
[6 empty] | 5 | MCU Temp. Error Code | 0 = No Error 1 = Out of Temp. 2 = Over Temp. 3 = Under Temp. 255 = Communication Fail |  | 5 | Leakage Port 6
[6 empty] | 6 | PT-100 Temp. 1 Error Code | 0 = No Error 1 = Out of Temp. 2 = Over Temp. 3 = Under Temp. |  | 6 | - | -
[6 empty] | 7 | PT-100 Temp. 2 Error Code |  |  | 7 | I2C COM Status | 0: Online 1: Offline
[6 empty] | 8 | PT-100 Temp. 3 Error Code
[6 empty] | 9 | PT-100 Temp. 4 Error Code |  |  | PSU Error Code Byte
[6 empty] | 10 | Supply Flow Temp. Error Code |  |  | Bit Index | Content | Comment
[6 empty] | 11 | Primary Outlet FlowTemp. Error Code |  |  | 0 | Temperature Fault | 0: No 1: Yes
[6 empty] | 12 | Supply Flow 1 Error Code | 0 = No Error 1 = Out of Flow 2 = Over Flow 3 = Under Flow |  | 1 | Vin Fault
[6 empty] | 13 | Primary Outlet Flow 2 Error Code |  |  | 2 | Iout Fault
[6 empty] | 14 | Leakage Error Code | see Table beside |  | 3 | Vout Fault
[6 empty] | 15 | Level Error Code | 0 = No Error 1 = Low Tank Level |  | 4 | Power OFF
[6 empty] | 16 | Pump 1 Error Code | 0 = No Error 1 = Stalled 2 = Over Speed 3 = Under Speed 4 = Out of Control |  | 5 | FAN Fault
[6 empty] | 17 | Pump 2 Error Code |  |  | 6 | Power not good
[6 empty] | 18 | Pump 3 Error Code |  |  | 7 | I2C COM Status | 0: Online 1: Offline
[6 empty] | 19 | FAN Row A1 Error Code
[6 empty] | 20 | FAN Row A2 Error Code
[6 empty] | 21 | FAN Row A3 Error Code
[6 empty] | 22 | FAN Row A4 Error Code
[6 empty] | 23 | FAN Row A5 Error Code
[6 empty] | 24 | FAN Row B1 Error Code
[6 empty] | 25 | FAN Row B2 Error Code
[6 empty] | 26 | FAN Row B3 Error Code
[6 empty] | 27 | FAN Row B4 Error Code
[6 empty] | 28 | FAN Row B5 Error Code
[6 empty] | 29 | PSU 1 Error Code | see Table beside
[6 empty] | 30 | PSU 2 Error Code
[6 empty] | 31 | PSU 3 Error Code
[6 empty] | 32 | FAN Group 0 - FAN #1 Error Code | 0 = No Error 1 = Stalled 2 = Over Speed 3 = Under Speed 4 = Out of Control 255 = Communication Fail
[6 empty] | 33 | FAN Group 0 - FAN #2 Error Code
[6 empty] | 34 | FAN Group 0 - FAN #3 Error Code
[6 empty] | 35 | FAN Group 0 - FAN #4 Error Code
[6 empty] | 36 | FAN Group 1 - FAN #1 Error Code
[6 empty] | 37 | FAN Group 1 - FAN #2 Error Code
[6 empty] | 38 | FAN Group 1 - FAN #3 Error Code
[6 empty] | 39 | FAN Group 1 - FAN #4 Error Code
[6 empty] | 40 | FAN Group 2 - FAN #1 Error Code
[6 empty] | 41 | FAN Group 2 - FAN #2 Error Code
[6 empty] | 42 | FAN Group 2 - FAN #3 Error Code
[6 empty] | 43 | FAN Group 2 - FAN #4 Error Code
[6 empty] | 44 | FAN Group 3 - FAN #1 Error Code
[6 empty] | 45 | FAN Group 3 - FAN #2 Error Code
[6 empty] | 46 | FAN Group 3 - FAN #3 Error Code
[6 empty] | 47 | FAN Group 3 - FAN #4 Error Code
[6 empty] | 48 | FAN Group 4 - FAN #1 Error Code
[6 empty] | 49 | FAN Group 4 - FAN #2 Error Code
[6 empty] | 50 | FAN Group 4 - FAN #3 Error Code
[6 empty] | 51 | FAN Group 4 - FAN #4 Error Code
[6 empty] | 52 | Temperature Control Error | 0 = No Error 1 = Out of Command Range
[6 empty] | 53 | Pressure Drop Control Error Code
[6 empty] | 54 | Flow Control Error Code
5 | Firmware Update
| Query (0x50) | Entry Bootloader Command
Host:
|  | Byte Index | Content | Comment | Remark
|  | 0 | Command ID | As title | see ' CDU Bootloader Command ID '
|  | 1 | Sub Command | 0x80 = Entry Bootloader
6 | Set Configuration
| Query (0xE0) | Pressure Sensors Max/Min Alarm Configuration
|  | Host: |  |  |  | CDU:
|  | Byte Index | Content | Comment | Remark | Byte Index | Content | Comment
|  | 0 | Command ID | As title |  | 0 | Command ID | As title
|  | 1 | Return Pressure 1 Max | LSB | Unit: 0.01 psi Format: uint16 Range: 0 ~ 10000
|  | 2 |  | HSB
|  | 3 | Return Pressure 1 Min | LSB
|  | 4 |  | HSB
|  | 5 | Supply Pressure 2 Max | LSB
|  | 6 |  | HSB
|  | 7 | Supply Pressure 2 Min | LSB
|  | 8 |  | HSB
|  | 9 | Primary Inlet Pressure 3 Max | LSB
|  | 10 |  | HSB
|  | 11 | Primary Inlet Pressure 3 Min | LSB
|  | 12 |  | HSB
|  | 13 | Primary Outlet Pressure 4 Max | LSB
|  | 14 |  | HSB
|  | 15 | Primary Outlet Pressure 4 Min | LSB
|  | 16 |  | HSB
| Query (0xE1) | Temperature Sensors Max/Min Alarm Configuration
|  | Host: |  |  |  | CDU:
|  | Byte Index | Content | Comment | Remark | Byte Index | Content | Comment
|  | 0 | Command ID | As title |  | 0 | Command ID | As title
|  | 1 | MCU Temperature Max | LSB | Unit: 0.01 °C Format: int16 Range: -2500 ~ 10000
|  | 2 |  | HSB
|  | 3 | MCU Temperature Min | LSB
|  | 4 |  | HSB
|  | 5 | PT-100 Temperature 1 Max | LSB | Unit: 0.01 °C Format: int16 Range: -4000 ~ 12500
|  | 6 |  | HSB
|  | 7 | PT-100 Temperature 1 Min | LSB
|  | 8 |  | HSB
|  | 9 | PT-100 Temperature 2 Max | LSB
|  | 10 |  | HSB
|  | 11 | PT-100 Temperature 2 Min | LSB
|  | 12 |  | HSB
|  | 13 | PT-100 Temperature 3 Max | LSB
|  | 14 |  | HSB
|  | 15 | PT-100 Temperature 3 Min | LSB
|  | 16 |  | HSB
|  | 17 | PT-100 Temperature 4 Max | LSB
|  | 18 |  | HSB
|  | 19 | PT-100 Temperature 4 Min | LSB
|  | 20 |  | HSB
|  | 21 | Supply Flow Temperature Max | LSB | Unit: 0.01 °C Format: int16 Range: -2500 ~ 15000
|  | 22 |  | HSB
|  | 23 | Supply Flow Temperature Min | LSB
|  | 24 |  | HSB
|  | 25 | Primary Outlet Flow Temperature Max | LSB
|  | 26 |  | HSB
|  | 27 | Primary Outlet Flow Temperature Min | LSB
|  | 28 |  | HSB
| Query (0xE2) | Flow Sensors Max/Min Alarm Configuration
|  | Host: |  |  |  | CDU:
|  | Byte Index | Content | Comment | Remark | Byte Index | Content | Comment
|  | 0 | Command ID | As title |  | 0 | Command ID | As title
|  | 1 | Supply Flow Max | LSB | Unit: 0.01 cm/s Format: uint16 Range: 1000 ~ 40000
|  | 2 |  | HSB
|  | 3 | Supply Flow Min | LSB
|  | 4 |  | HSB
|  | 5 | Primary Outlet Flow Max | LSB
|  | 6 |  | HSB
|  | 7 | Primary Outlet Flow Min | LSB
|  | 8 |  | HSB
| Query (0xE3) | Pumps/FANs Speed Max/Min Alarm Configuration
|  | Host: |  |  |  | CDU:
|  | Byte Index | Content | Comment | Remark | Byte Index | Content | Comment
|  | 0 | Command ID | As title |  | 0 | Command ID | As title
|  | 1 | Pump Speed Max | LSB | Unit: RPM Format: uint32 Range: 0 ~ 99999
|  | 2 |  | HSB
|  | 3 |  | USB
|  | 4 |  | MSB
|  | 5 | Pump Speed Min | LSB
|  | 6 |  | HSB
|  | 7 |  | USB
|  | 8 |  | MSB
|  | 9 | Fan Speed Max | LSB
|  | 10 |  | HSB
|  | 11 |  | USB
|  | 12 |  | MSB
|  | 13 | Fan Speed Min | LSB
|  | 14 |  | HSB
|  | 15 |  | USB
|  | 16 |  | MSB
| Query (0xE4) | Auto Control Max/Min Alarm Configuration
|  | Host: |  |  |  | CDU:
|  | Byte Index | Content | Comment | Remark | Byte Index | Content | Comment
|  | 0 | Command ID | As title |  | 0 | Command ID | As title
|  | 1 | Temperature Command Ratio Range | 0 ~ 100 (%)
|  | 2 | Pressure Command Ratio Range
|  | 3 | Flow Command Ratio Range
Reserved for RD
| Query (0xEE) | Alarm Time Trigger Configuration
|  | Host: |  |  |  | CDU:
|  | Byte Index | Content | Comment | Remark | Byte Index | Content | Comment
|  | 0 | Command ID | As title |  | 0 | Command ID | As title
|  | 1 | Pressure Sensors Max/Min Trigger Time | LSB | Unit: Second Format: uint16 Range: 0 ~ 65535
|  | 2 |  | HSB
|  | 3 | Temperature Sensors Max/Min Trigger Time | LSB
|  | 4 |  | HSB
|  | 5 | Flow Sensors Max/Min Trigger Time | LSB
|  | 6 |  | HSB
|  | 7 | Pumps/FANs Speed Max/Min Trigger Time | LSB
|  | 8 |  | HSB
|  | 9 | Temperature Control Max/Min Trigger Time | LSB
|  | 10 |  | HSB
|  | 11 | Pressure Control Max/Min Trigger Time | LSB
|  | 12 |  | HSB
|  | 13 | Flow Control Max/Min Trigger Time | LSB
|  | 14 |  | HSB
| Query (0xEF) | PID Contorl Configuration
|  | Host: |  |  |  | CDU:
|  | Byte Index | Content | Comment | Remark | Byte Index | Content | Comment
|  | 0 | Command ID | As title |  | 0 | Command ID | As title
|  | 1 | Control Type | 0 ~ 2 | 0 = Temperature Control 1 = Pressure Control 2 = Flow Control | 1 | Control Type | 0 ~ 2
|  | 2 | Control Speed | 1 ~ 100 (Hz)
|  | 3 | Control Resolution | LSB | Format: uint16 Range: 1 ~ 65535
|  | 4 |  | HSB
|  | 5 | Proportional Gain | LSB | Format: uint16 Range: 0 ~ 65535 Real Gain = (Value / Control Resolution / Control Speed)
|  | 6 |  | HSB
|  | 7 | Integral Gain | LSB
|  | 8 |  | HSB
|  | 9 | Derivative Gain | LSB
|  | 10 |  | HSB

## 工作表1
Setting Mode |  | Value | HEX | PID Contorl Configuration |  | Value | HEX
| SOH |  | AA |  | SOH |  | AA
| BMC |  | 42 |  | BMC |  | 42
| CDU |  | 43 |  | CDU |  | 43
| Length of Payload | 17 | 11 |  | Length of Payload | 11 | 0B
0 | Command ID | 1 | 01 | 0 | Command ID |  | EF
1 | Set Mode | 255 | FF | 1 | Control Type | 0 | 00
2 | Target Temperature | 45 | 2D | 2 | Control Speed | 10 | 0A
3 | Target Pressure | 50 | 32 | 3 | Control Resolution | 1000 | E8
4 | Target Flow | 20 | 14 | 4 |  |  | 03
5 |  |  | 00 | 5 | Proportional Gain | 1000 | E8 | Kp
6 | Valve Gate | 50 | 32 | 6 |  |  | 03 | 0.1
7 | Pump 1 PWM | 100 | 64 | 7 | Integral Gain | 2 | 02 | Ki
8 | Pump 2 PWM | 100 | 64 | 8 |  |  | 00 | 0.0002
9 | Pump 3 PWM | 100 | 64 | 9 | Derivative Gain | 6550 | 96 | Kd
10 | FAN Row A PWM | 0 | 00 | 10 |  |  | 19 | 0.655
11 | FAN Row B PWM | 0 | 00 |  | Checksum | 1040 | 10
12 | FAN Group 0 PWM | 0 | 00 | AA 42 43 0B EF 00 0A E8 03 E8 03 02 00 96 19 10
13 | FAN Group 1 PWM | 0 | 00
14 | FAN Group 2 PWM | 0 | 00
15 | FAN Group 3 PWM | 0 | 00
16 | FAN Group 4 PWM | 0 | 00
| Checksum | 871 | 67
AA 42 43 11 01 FF 2D 32 14 00 32 64 64 64 00 00 00 00 00 00 00 67
| SOH |  | AA
| BMC |  | 42
| CDU |  | 43 |  | cdustm32io-tools -t 11 n 2 100 0 0 0 0 0 0 0 0 0 0 0 0 0 0
| Length of Payload | 17 | 11
0 | Command ID | 1 | 01
1 | Set Mode | 2 | 02
2 | Target Temperature | 50 | 32
3 | Target Pressure | 30 | 1E
4 | Target Flow | 0 | 00
5 |  |  | 00
6 | Valve Gate | 0 | 0
7 | Pump 1 PWM | 80 | 50
8 | Pump 2 PWM | 80 | 50
9 | Pump 3 PWM | 80 | 50
10 | FAN Row A PWM | 0 | 00
11 | FAN Row B PWM | 0 | 00
12 | FAN Group 0 PWM | 0 | 00
13 | FAN Group 1 PWM | 0 | 00
14 | FAN Group 2 PWM | 0 | 00
15 | FAN Group 3 PWM | 0 | 00
16 | FAN Group 4 PWM | 0 | 00
| Checksum | 473 | D9
AA 42 43 11 01 02 32 1E 00 00 0 50 50 50 00 00 00 00 00 00 00 D9

## CDU_Bootloader_Command_ID
Application Command ID
Physical Layer
| Symbol | Value
| Baud Rate | 115200
| Parity Bit | None
| Data Bit | 8
| Stop Bit | 1
Basic Frame
| Byte Index | 0 | n
| Data | Handle Command | Program Payload
|  | < Request > |  |  |  | < Reply >
1 | Handle Command
| Query (0x01) | Bootloader Version Information
|  | Host: |  |  |  | CDU:
|  | Byte Index | Content | Comment |  | Byte Index | Content | Comment
|  | 0 | Command ID | As title |  | 0 | Command ID | As title
[6 empty] | 1 | Bootloader Version
[6 empty] | 2 | Bootloader Reversion
| Query (0x02) | Erase Flash
|  | Host: |  |  |  | CDU:
|  | Byte Index | Content | Comment |  | Byte Index | Content | Comment
|  | 0 | Command ID | As title |  | 0 | Command ID | As title
| Query (0x03) | Program Flash
|  | Host: |  |  |  | CDU:
|  | Byte Index | Content | Comment | Remark | Byte Index | Content | Comment
|  | 0 | Command ID | As title | https://en.wikipedia.org/wiki/Intel_HEX | 0 | Command ID | As title
|  | 1 | intel HEX File | 1. Remove start code ' : ' 2. Split into Byte 3. Max. n = 500
2
3
…
n
| ex. | if program payload n = 28
|  | Byte Index | Byte Data Hex
|  | 0 | 0x03
|  | 1 | 0x02
|  | 2 | 0x00
|  | 3 | 0x00
|  | 4 | 0x04
|  | 5 | 0x1D
|  | 6 | 0x00
|  | 7 | 0xDD
|  | 8 | 0x10
…
|  | 28 | 0xA4
| Query (0x04) | Read CRC16 Command
|  | Host: |  |  |  | CDU:
|  | Byte Index | Content | Comment | Remark | Byte Index | Content | Comment
|  | 0 | Command ID | As title | Address Range: 0x9D000000~0x9D0FF000 The Read CRC command is used to verify the content of the program Flash after programming. | 0 | Command ID | As title
|  | 1 | Program Address | 0x00 |  | 1 | CRC16 | LSB
|  | 2 |  | 0x00 |  | 2 |  | HSB
|  | 3 |  | 0x00
|  | 4 |  | 0x9D
|  | 5 | Program Data Length | 0x00
|  | 6 |  | 0xF0
|  | 7 |  | 0x0F
|  | 8 |  | 0x00
|  | 9 | CRC16 | LSB
|  | 10 |  | HSB
| Query (0x05) | Exit Bootloader Command
Host:
|  | Byte Index | Content | Comment | Remark
|  | 0 | Command ID | As title | see ' Application Command ID '
BMC
CDU
UART
Payload: n bytes
Entry Bootloader
Entry command(ex. 0x50, 0x80)
Return Bootloader ACK
Bootloader information(ex. 0x01, 0x03,0x64)
Erase Flash
Erase command(ex. 0x02)
Return Erase Flash ACK
Erase Flash OK(ex. 0x02)
Application
Bootloader
Program firmware n Payload
Program command(ex. 0x03, 0x02, 0x00,…,0xA4)
Return Program Flash ACK
Program Flash OK(ex. 0x03)
Read CRC16
Read CRC16 command(ex. 0x04, addr, length, crc16)
Return CRC16 ACK
CRC16 command(ex. 0x04, crc16)
Check Application information
Read command(ex. 0xF3, 0x01)
Exit Bootloader
Exit command(ex. 0x05)
Return Application ACK
Application command(ex. 0xF3, 0x03, 0x65, 0x03, 0x64)
Application
Check Bootloader information
Read command(ex. 0x01)

## Config整合 (hidden)
項目 | Config項目 | ALCDU | LLCDU | HRU
Pump示警(低) | PUMP_RPM_LOW | V | V | V
Pump示警(高) | PUMP_RPM_HIGH | V | V | V
Fan示警(低) | FAN_RPM_LOW | V |  | V
Fan示警(高) | FAN_RPM_HIGH | V |  | V
壓力1示警(低) | PRESSURE1_LOW | V | V | V
壓力1示警(高) | PRESSURE1_HIGH | V | V | V
壓力2示警(低) | PRESSURE2_LOW | V | V | V
壓力2示警(高) | PRESSURE2_HIGH | V | V | V
壓力3示警(低) | PRESSURE3_LOW
壓力3示警(高) | PRESSURE3_HIGH
壓力4示警(低) | PRESSURE4_LOW
壓力4示警(高) | PRESSURE4_HIGH
NTC1示警(低) | NTC1_HIGH | V | V | V | 舊有機種有未來沒有
NTC1示警(高) | NTC1_LOW | V | V | V | 舊有機種有未來沒有
NTC2示警(低) | NTC2_HIGH | V | V | V | 舊有機種有未來沒有
NTC2示警(高) | NTC2_LOW | V | V | V | 舊有機種有未來沒有
PT100 1示警(低) | PT100_1_Alarm_L | V | V | V
PT100 1示警(高) | PT100_1_Alarm_H | V | V | V
PT100 2示警(低) | PT100_2_Alarm_L
PT100 2示警(高) | PT100_2_Alarm_H
PT100 3示警(低) | PT100_3_Alarm_L
PT100 3示警(高) | PT100_3_Alarm_H
LIQUID_FLOW1(低) | LIQ_FL1_Alarm_L
LIQUID_FLOW1(高) | LIQ_FL1_Alarm_H
LIQUID_FLOW2 (低) | LIQ_FL2_Alarm_L
LIQUID_FLOW2(高) | LIQ_FL2_Alarm_H
LIQUID_FLOW1_Temp(低) | LIQ_FL1_T_Arm_L
LIQUID_FLOW1_Temp(高) | LIQ_FL1_T_Arm_H
LIQUID_FLOW2_Temp(低) | LIQ_FL2_T_Arm_L
LIQUID_FLOW2_Temp(高) | LIQ_FL2_T_Arm_H
目標PT100 4示警(低，高) | PT100_4_TARGET | V | V | V
目標流量示警(低，高) | FLOW_TARGET | V | V | V
目標壓差示警(低，高) | PRESSURE_DIFF_TARGET_HIGH | V | V | V
目標FXFF101溫度 | FXFF101_TARGET | V | V | V
目標流量 | FLOW_TARGET | V | V | V
目標壓差 | PRESSURE_DIFF_TARGET | V | V | V
目標壓差Range(%) | PRESSURE_DIFF_RANGE | V | V | V
目標流量Range(%) | FLOW_RANGE | V | V | V
目標FXFF101溫度Range(%) | FXFF101_TEMP_RANGE | V | V | V
風扇反應時間 | FAN1_ADD_RESP_TIME | V |  | V
比例閥反應時間 | Proportional_valve_ADD_RESP_TIME |  | V
Pump反應時間 | PUMP_ADD_RESP_TIME | V | V | V

## Redfish_Name
分類 | Unit | Redfish API名稱 | Application Command ID | Byte Index | HRU | LLCDU | ALCDU | Max Value | Min Value | Alarm_max | Alarm_min | Alarm_max定值 | Alarm_min定值
Firmware Version Information |  | Application_Ver | 0xF3 | Byte 1 | V | V | V
|  | Application_Rev |  | Byte 2 | V | V | V
|  | Bootloader_Ver |  | Byte 3 | V | V | V
|  | Bootloader Rev |  | Byte 4 | V | V | V
壓力項 (kpa/psi) | 0.01 kpa | Pr_Liq_Return | 0x10 | Byte 1/2 | V | V | V | 65535 | 0 | (Command ID)0xE0 Byte 1/2 | (Command ID)0xE0 Byte 3/4 | 600 | 0
|  | Pr_Liq_Supply |  | Byte 3/4 | V | V | V |  |  | (Command ID)0xE0 Byte 5/6 | (Command ID)0xE0 Byte 7/8 | 600 | 0
|  | Pr_Liq_DP |  |  | V | V | V |  |  |  |  | 600 | 0 | Pr Liq Supply減Pr Liq Return
|  | Pr_Primary_In (預留) |  | Byte 5/6 | X | X | X |  |  | (Command ID)0xE0 Byte 9/10 | (Command ID)0xE0 Byte 11/12 | 600 | 0
|  | Pr_Primary_Out (LL) |  | Byte 7/8 | X | V | X |  |  | (Command ID)0xE0 Byte 13/14 | (Command ID)0xE0 Byte 15/16 | 600 | 0
溫度項 (度C/度F) | 0.01 °C | Temp_Air_Temp_In | 0x11 |  |  | X
|  | Temp_Air_Temp_Out |  |  |  | X
|  | Temp_Liq_Return |  | Byte 3/4 | V | V | V | 12500 | -4000 | (Command ID)0xE1 Byte 5/6 | (Command ID)0xE1 Byte 7/8 | 65 | 15
|  | Temp_Liq_Supply |  | Byte 5/6 | V | V | V | 12500 | -4000 | (Command ID)0xE1 Byte 9/10 | (Command ID)0xE1 Byte 11/12 | 65 | 15
|  | Temp_MCU |  | Byte 1/2 | V | V | V | 10000 | -2500 | (Command ID)0xE1 Byte 1/2 | (Command ID)0xE1 Byte 3/4 | 65 | 15
|  | Temp_Pri_In (LL) |  | Byte 7/8 | X | V | X | 12500 | -4000 | (Command ID)0xE1 Byte 13/14 | (Command ID)0xE1 Byte 15/16 | 65 | 15
|  | Temp_Pri_Out (LL) |  | Byte 9/10 | X | V | X | 12500 | -4000 | (Command ID)0xE1 Byte 17/18 | (Command ID)0xE1 Byte 19/20 | 65 | 15
|  | Temp_Flow_Sup (預留) 自動控制 |  | Byte 11/12 | X | X | X | 15000 | -2500 | (Command ID)0xE1 Byte 21/22 | (Command ID)0xE1 Byte 23/24 | 65 | 15
|  | Temp_Pri_Out (預留) |  | Byte 13/14 | X | X | X | 15000 | -2500 | (Command ID)0xE1 Byte 25/26 | (Command ID)0xE1 Byte 27/28 | 65 | 15
流量 | 0.01 L/s | Flow_Supply | 0x12 | Byte 1/2 | V | V | V | 750 | 0 | (Command ID)0xE2 Byte 1/2 | (Command ID)0xE2 Byte 3/4 | 7 | 0
|  | Flow_Pri_Out |  | Byte 3/4 | X | V | X |  |  | Byte 5/6 | Byte 7/8 | 7 | 0
Valve Gate | % | Primary_Valve (LL) | 0x13 | Byte 1 | X | V | X | 100 | 0
Water_Detect | - | Water_Detect_1 | 0x14 | Byte 1 | V | V | V | 5 | 0 |  |  | Alarm值為4 | Alarm值為4
|  | Water_Detect_2 |  | Byte 2 | V | V | V |  |  |  |  | Alarm值為4 | Alarm值為4
|  | Water_Detect_3 (風扇牆) |  | Byte 3 | V | X | X |  |  |  |  | Alarm值為4 | Alarm值為4
|  | Water_Detect_4 (風扇牆) |  | Byte 4 | V | X | X |  |  |  |  | Alarm值為4 | Alarm值為4
|  | Water_Detect_5 (預留) |  | Byte 5 | X | X | X |  |  |  |  | Alarm值為4 | Alarm值為4
|  | Water_Detect_6 (預留) |  | Byte 6 | X | X | X |  |  |  |  | Alarm值為4 | Alarm值為4
Level Sensors | - | Tank_Level (一樣) | 0x16 | Byte 1 | V | V | V | 3 | 0 |  |  | Alarm值為0 | Alarm值為0
Pumps Information | RPM | RPM_P1 | 0x18 | Byte 2/3/4/5 | V | V | V | 9000 | 0 | (Command ID)0xE3 Byte 1/2/3/4 | (Command ID)0xE2 Byte 5/6/7/8 | 8000 | 0
|  | RPM_P2 |  | Byte 7/8/9/10 | V | V | V |  |  |  |  | 8000 | 0
|  | RPM_P3 |  | Byte 12/13/14/15 | V | V | X |  |  |  |  | 8000 | 0
| % | PWM_P1 |  | Byte 1 | V | V | V | 100 | 0
|  | PWM_P2 |  | Byte 6 | V | V | V
|  | PWM_P3 |  | Byte 11 | V | V | X
FAN Row A / B Information | RPM | RPM_RowA_F1 | 0x19 | Byte 2/3/4/5 | X | X | V | 20000 | 0 | (Command ID)0xE3 Byte 9/10/11/12 | (Command ID)0xE3 Byte 13/14/15/16 | 18000
|  | RPM_RowA_F2 |  | Byte 6/7/8/9 | X | X | V |  |  |  |  | 18000
|  | RPM_RowA_F3 |  | Byte 10/11/12/13 | X | X | V |  |  |  |  | 18000
|  | RPM_RowA_F4 |  | Byte 14/15/16/17 | X | X | V |  |  |  |  | 18000
|  | RPM_RowA_F5 |  | Byte 18/19/20/21 | X | X | V |  |  |  |  | 18000
|  | RPM_RowB_F1 |  | Byte 23/24/25/26 | X | X | V |  |  |  |  | 18000
|  | RPM_RowB_F2 |  | Byte 27/28/29/30 | X | X | V |  |  |  |  | 18000
|  | RPM_RowB_F3 |  | Byte 31/32/33/34 | X | X | V |  |  |  |  | 18000
|  | RPM_RowB_F4 |  | Byte 35/36/37/38 | X | X | V |  |  |  |  | 18000
|  | RPM_RowB_F5 |  | Byte 39/40/41/42 | X | X | V |  |  |  |  | 18000
| % | PWM_RowA_Fan |  | Byte 1 | X | X | V | 100 | 0
|  | PWM_RowB_Fan |  | Byte 22 | X | X | V
PSUs Information | 0.1W | Power_PSU1 | 0x1A | Byte 1/2 | V | V | V | 13000 | 0
|  | Power_PSU2 |  | Byte 7/8 | V | V | V
|  | Power_PSU3 |  | Byte 13/14 | V | V | V
| 0.1 V | Voltage_PSU1 |  | Byte 3/4 | V | V | V | 512 | 0
|  | Voltage_PSU2 |  | Byte 9/10 | V | V | V
|  | Voltage_PSU3 |  | Byte 15/16 | V | V | V
| 0.1 A | Current_PSU1 |  | Byte 5/6 | V | V | V | 256 | 0
|  | Current_PSU2 |  | Byte 11/12 | V | V | V
|  | Current_PSU3 |  | Byte 17/18 | V | V | V
FAN Door Information | % | PWM_RowA_FDoor | 0x1B, 0x00 | Byte 1 | V | X | X | 100 | 0
| RPM | RPM_FDoor_A1 |  | Byte 2/3/4/5 | V | X | X | 9000 | 0 | (Command ID)0xE3 Byte 9/10/11/12 | (Command ID)0xE3 Byte 13/14/15/16 | 8500
|  | RPM_FDoor_A2 |  | Byte 6/7/8/9 | V | X | X |  |  |  |  | 8500
|  | RPM_FDoor_A3 |  | Byte 10/11/12/13 | V | X | X |  |  |  |  | 8500
|  | RPM_FDoor_A4 |  | Byte 14/15/16/17 | V | X | X |  |  |  |  | 8500
| 0.1 A | Current_FDoor_A1 |  | Byte 18/19 | V | X | X | 256 | 0
|  | Current_FDoor_A2 |  | Byte 20/21 | V | X | X
|  | Current_FDoor_A3 |  | Byte 22/23 | V | X | X
|  | Current_FDoor_A4 |  | Byte 24/25 | V | X | X
| 0.01 CFM | Air_Velocity_A |  | Byte 26/27 | V | X | X | 30000 | 0 |  |  | 後補
| 0.01 °C | Temp_Air_In_A |  | Byte 28/29 | V | X | X | 12800 | -12800 |  |  | 65 | 15
|  | Temp_Air_Out_A |  | Byte 30/31 | V | X | X |  |  |  |  | 65 | 15
| % | PWM_RowB_FDoor | 0x1B, 0x01 | Byte 1 | V | X | X | 100 | 0
| RPM | RPM_FDoor_B1 |  | Byte 2/3/4/5 | V | X | X | 9000 | 0 | (Command ID)0xE3 Byte 9/10/11/12 | (Command ID)0xE3 Byte 13/14/15/16 | 8500
|  | RPM_FDoor_B2 |  | Byte 6/7/8/9 | V | X | X |  |  |  |  | 8500
|  | RPM_FDoor_B3 |  | Byte 10/11/12/13 | V | X | X |  |  |  |  | 8500
|  | RPM_FDoor_B4 |  | Byte 14/15/16/17 | V | X | X |  |  |  |  | 8500
| 0.1 A | Current_FDoor_B1 |  | Byte 18/19 | V | X | X | 256 | 0
|  | Current_FDoor_B2 |  | Byte 20/21 | V | X | X
|  | Current_FDoor_B3 |  | Byte 22/23 | V | X | X
|  | Current_FDoor_B4 |  | Byte 24/25 | V | X | X
| 0.01 CFM | Air_Velocity_B |  | Byte 26/27 | V | X | X | 30000 | 0 |  |  | 後補
| 0.01 °C | Temp_Air_In_B |  | Byte 28/29 | V | X | X | 12800 | -12800 |  |  | 65 | 15
|  | Temp_Air_Out_B |  | Byte 30/31 | V | X | X |  |  |  |  | 65 | 15
| % | PWM_RowC_FDoor | 0x1B, 0x02 | Byte 1 | V | X | X | 100 | 0
| RPM | RPM_FDoor_C1 |  | Byte 2/3/4/5 | V | X | X | 9000 | 0 | (Command ID)0xE3 Byte 9/10/11/12 | (Command ID)0xE3 Byte 13/14/15/16 | 8500
|  | RPM_FDoor_C2 |  | Byte 6/7/8/9 | V | X | X |  |  |  |  | 8500
|  | RPM_FDoor_C3 |  | Byte 10/11/12/13 | V | X | X |  |  |  |  | 8500
|  | RPM_FDoor_C4 |  | Byte 14/15/16/17 | V | X | X |  |  |  |  | 8500
| 0.1 A | Current_FDoor_C1 |  | Byte 18/19 | V | X | X | 256 | 0
|  | Current_FDoor_C2 |  | Byte 20/21 | V | X | X
|  | Current_FDoor_C3 |  | Byte 22/23 | V | X | X
|  | Current_FDoor_C4 |  | Byte 24/25 | V | X | X
| 0.01 CFM | Air_Velocity_C |  | Byte 26/27 | V | X | X | 30000 | 0 |  |  | 後補
| 0.01 °C | Temp_Air_In_C |  | Byte 28/29 | V | X | X | 12800 | -12800 |  |  | 65 | 15
|  | Temp_Air_Out_C |  | Byte 30/31 | V | X | X |  |  |  |  | 65 | 15
| % | PWM_RowD_FDoor | 0x1B, 0x03 | Byte 1 | V | X | X | 100 | 0
| RPM | RPM_FDoor_D1 |  | Byte 2/3/4/5 | V | X | X | 9000 | 0 | (Command ID)0xE3 Byte 9/10/11/12 | (Command ID)0xE3 Byte 13/14/15/16 | 8500
|  | RPM_FDoor_D2 |  | Byte 6/7/8/9 | V | X | X |  |  |  |  | 8500
|  | RPM_FDoor_D3 |  | Byte 10/11/12/13 | V | X | X |  |  |  |  | 8500
|  | RPM_FDoor_D4 |  | Byte 14/15/16/17 | V | X | X |  |  |  |  | 8500
| 0.1 A | Current_FDoor_D1 |  | Byte 18/19 | V | X | X | 256 | 0
|  | Current_FDoor_D2 |  | Byte 20/21 | V | X | X
|  | Current_FDoor_D3 |  | Byte 22/23 | V | X | X
|  | Current_FDoor_D4 |  | Byte 24/25 | V | X | X
| 0.01 CFM | Air_Velocity_D |  | Byte 26/27 | V | X | X | 30000 | 0 |  |  | 後補
| 0.01 °C | Temp_Air_In_D |  | Byte 28/29 | V | X | X | 12800 | -12800 |  |  | 65 | 15
|  | Temp_Air_Out_D |  | Byte 30/31 | V | X | X |  |  |  |  | 65 | 15
| % | PWM_RowE_FDoor | 0x1B, 0x04 | Byte 1 | V | X | X | 100 | 0
| RPM | RPM_FDoor_E1 |  | Byte 2/3/4/5 | V | X | X | 9000 | 0 | (Command ID)0xE3 Byte 9/10/11/12 | (Command ID)0xE3 Byte 13/14/15/16 | 8500
|  | RPM_FDoor_E2 |  | Byte 6/7/8/9 | V | X | X |  |  |  |  | 8500
|  | RPM_FDoor_E3 |  | Byte 10/11/12/13 | V | X | X |  |  |  |  | 8500
|  | RPM_FDoor_E4 |  | Byte 14/15/16/17 | V | X | X |  |  |  |  | 8500
| 0.1 A | Current_FDoor_E1 |  | Byte 18/19 | V | X | X | 256 | 0
|  | Current_FDoor_E2 |  | Byte 20/21 | V | X | X
|  | Current_FDoor_E3 |  | Byte 22/23 | V | X | X
|  | Current_FDoor_E4 |  | Byte 24/25 | V | X | X
| 0.01 CFM | Air_Velocity_E |  | Byte 26/27 | V | X | X | 30000 | 0 |  |  | 後補
| 0.01 °C | Temp_Air_In_E |  | Byte 28/29 | V | X | X | 12800 | -12800 |  |  | 65 | 15
|  | Temp_Air_Out_E |  | Byte 30/31 | V | X | X |  |  |  |  | 65 | 15
網頁上名稱 (要給)
控制 |  | TMP + PSR Auto Mode | 0x01 | index 2 + 3
|  | TMP + Flow Auto Mode |  | index 2 + 4~5
|  | TMP Auto + Pump PWM Manual |  | index 2 + 7~9
|  | PSR Auto + Valve/FAN PWM Manual |  | index 3 + 6 / 10~11 / 12~16
|  | Flow Auto + Valve/FAN PWM Manual |  | index 4~5 + 6 / 10~11 / 12~16
|  | Manual Mode |  | index 6~16
CDU Target Command Information |  | Set_Mode | 0x02 | index 1
|  | Target_Temp |  | index 2
|  | Target_Pressure |  | index 3
|  | Target_Flow |  | index 4/5
Error Event |  | Err_Pr_Liq_Return | 0x20 | index 1
|  | Err_Pr_Liq_Supply |  | index 2
|  | Err_Pr_Pri_In |  | index 3
|  | Err_Pr_Pri_Out |  | index 4
|  | Err_T_MCU |  | index 5
|  | Err_T_Liq_Return |  | index 6
|  | Err_T_Liq_Supply |  | index 7
|  | Err_T_Pri_In |  | index 8
|  | Err_T_Pri_Out |  | index 9
|  | Er_T_Flow_Supply |  | index 10
|  | Er_T_Flow_PriOut |  | index 11
|  | Err_Flow_Supply |  | index 12
|  | Err_Flow_Pri_out |  | index 13
|  | Err_Leakage |  | index 14
|  | Err_Tank_Level |  | index 15
|  | Err_RPM_P1 |  | index 16
|  | Err_RPM_P2 |  | index 17
|  | Err_RPM_P3 |  | index 18
|  | Err_RPM_RowA_F1 |  | index 19
|  | Err_RPM_RowA_F2 |  | index 20
|  | Err_RPM_RowA_F3 |  | index 21
|  | Err_RPM_RowA_F4 |  | index 22
|  | Err_RPM_RowA_F5 |  | index 23
|  | Err_RPM_RowB_F1 |  | index 24
|  | Err_RPM_RowB_F2 |  | index 25
|  | Err_RPM_RowB_F3 |  | index 26
|  | Err_RPM_RowB_F4 |  | index 27
|  | Err_RPM_RowB_F5 |  | index 28
|  | Err_PSU1_Power |  | index 29
|  | Err_PSU2_Power |  | index 30
|  | Err_PSU3_Power |  | index 31
|  | Err_FanDoorA1 |  | index 32
|  | Err_FanDoorA2 |  | index 33
|  | Err_FanDoorA3 |  | index 34
|  | Err_FanDoorA4 |  | index 35
|  | Err_FanDoorB1 |  | index 36
|  | Err_FanDoorB2 |  | index 37
|  | Err_FanDoorB3 |  | index 38
|  | Err_FanDoorB4 |  | index 39
|  | Err_FanDoorC1 |  | index 40
|  | Err_FanDoorC2 |  | index 41
|  | Err_FanDoorC3 |  | index 42
|  | Err_FanDoorC4 |  | index 43
|  | Err_FanDoorD1 |  | index 44
|  | Err_FanDoorD2 |  | index 45
|  | Err_FanDoorD3 |  | index 46
|  | Err_FanDoorD4 |  | index 47
|  | Err_FanDoorE1 |  | index 48
|  | Err_FanDoorE2 |  | index 49
|  | Err_FanDoorE3 |  | index 50
|  | Err_FanDoorE4 |  | index 51
|  | Err_Temp Ctrl |  | index 52
|  | Err_Pr Drop Ctrl |  | index 53
|  | Err_Flow_Ctrl |  | index 54

## 網頁控&制端
Application Command ID
3 | Setting Mode
| Modify (0x01) | CDU Auto / Manual Mode Set
| 控制 | Host: |  |  |  | CDU:
|  | Byte Index | Content | Comment | Remark | Byte Index | Content | Comment
|  | 0 | Command ID | As title |  | 0 | Command ID | As title
|  | 1 | Set Mode | 0, 1 = Auto 2, 3, 4 = Auto + Manual 255 = Manual | 0 = TMP + PSR Auto Mode -> byte index 2 + 3 1 = TMP + Flow Auto Mode -> byte index 2 + 4~5 2 = TMP Auto + Pump PWM Manual -> byte index 2 + 7~9 3 = PSR Auto + Valve/FAN PWM Manual -> byte index 3 + 6 / 10~11 / 12~16 4 = Flow Auto + Valve/FAN PWM Manual -> byte index 4~5 + 6 / 10~11 / 12~16 255 = Manual Mode -> byte index 6~16 < Target Range > Temperature: 0 ~ 80 (°C) Pressure: 0 ~ 100 (psi) Flow: 10 ~ 400 (cm/s) | 1 | Set Mode | 0, 1 = Auto 2, 3, 4 = Auto + Manual 255 = Manual
|  | 2 | Target Temperature
|  | 3 | Target Pressure
|  | 4 | Target Flow | LSB
|  | 5 |  | HSB
|  | 6 | Valve Gate | 0 ~ 100 (%)
|  | 7 | Pump 1 PWM
|  | 8 | Pump 2 PWM
|  | 9 | Pump 3 PWM
|  | 10 | FAN Row A PWM
|  | 11 | FAN Row B PWM
|  | 12 | FAN Group 0 PWM | 0 ~ 100 (%)
|  | 13 | FAN Group 1 PWM
|  | 14 | FAN Group 2 PWM
|  | 15 | FAN Group 3 PWM
|  | 16 | FAN Group 4 PWM
網頁名稱
| Manual Control |  | Application Command ID | Byte Index
| AL | Pump PWM | 0x01 | Index 7/8
|  | Fan PWM | 0x01 | Index 10/11
| LL | Pump PWM | 0x01 | Index 7/8/9
|  | Primary Valve Value | 0x01 | Index 6
| HRU | Pump PWM | 0x01 | Index 7/8/9
|  | Fan PWM | 0x01 | Index 12/13/14/15/16
Automatic Control
Target Temperature
(下拉選單) | Constant Pressure Drop | Target Pressure Drop | 0x01 | Index 2/3
(下拉選單) | Flow | Target Flow | 0x01 | Index 2/4/5
6 | Set Configuration
| Query (0xE0) | Pressure Sensors Max/Min Alarm Configuration
|  | Host: |  |  |  | CDU:
|  | Byte Index | Content | Web name | Remark | Byte Index | Content | Comment
|  | 1 | Return Pressure 1 Max | Pressure Liquid Return Max | Unit: 0.01 psi Format: uint16 Range: 0 ~ 10000
|  | 3 | Return Pressure 1 Min | Pressure Liquid Return Min
|  | 5 | Supply Pressure 2 Max | Pressure Liquid Supply Max
|  | 7 | Supply Pressure 2 Min | Pressure Liquid Supply Min
|  | 9 | Primary Inlet Pressure 3 Max | Pressure Primary Inlet Max
|  | 11 | Primary Inlet Pressure 3 Min | Pressure Primary Inlet Min
|  | 13 | Primary Outlet Pressure 4 Max | Pressure Primary Outlet Max
|  | 15 | Primary Outlet Pressure 4 Min | Pressure Primary Outlet Min
| Query (0xE1) | Temperature Sensors Max/Min Alarm Configuration
|  | Host: |  |  |  | CDU:
|  | 0 | Command ID | Web name |  | 0 | Command ID | As title
|  | 1 | MCU Temperature Max | Temperature MCU Max | Unit: 0.01 °C Format: int16 Range: -2500 ~ 10000
|  | 3 | MCU Temperature Min | Temperature MCU Mim
|  | 5 | PT-100 Temperature 1 Max | Temperature Liquid Return Max | Unit: 0.01 °C Format: int16 Range: -4000 ~ 12500
|  | 7 | PT-100 Temperature 1 Min | Temperature Liquid Return Min
|  | 9 | PT-100 Temperature 2 Max | Temperature Liquid Supply Max
|  | 11 | PT-100 Temperature 2 Min | Temperature Liquid Supply Min
|  | 13 | PT-100 Temperature 3 Max | Temperature Primary Inlet Max
|  | 15 | PT-100 Temperature 3 Min | Temperature Primary Inlet Min
|  | 17 | PT-100 Temperature 4 Max | Temperature Primary Outlet Max
|  | 19 | PT-100 Temperature 4 Min | Temperature Primary Outlet Min
|  | 21 | Supply Flow Temperature Max | Temperature Flow Supply Max | Unit: 0.01 °C Format: int16 Range: -2500 ~ 15000
|  | 23 | Supply Flow Temperature Min | Temperature Flow Supply Min
|  | 25 | Primary Outlet Flow Temperature Max | Temperature Flow Primary Outlet Max
|  | 27 | Primary Outlet Flow Temperature Min | Temperature Flow Primary Outlet Min
| Query (0xE2) | Flow Sensors Max/Min Alarm Configuration
|  | Host: |  |  |  | CDU:
|  | Byte Index | Content | Web name | Remark | Byte Index | Content | Comment
|  | 2 | Supply Flow Max | Flow Liquid Max
|  | 3 | Supply Flow Min | Flow Liquid Min
|  | 5 | Primary Outlet Flow Max | Flow Primary Max
|  | 7 | Primary Outlet Flow Min | Flow Primary Min
| Query (0xE3) | Pumps/FANs Speed Max/Min Alarm Configuration
|  | Host: |  |  |  | CDU:
|  | Byte Index | Content | Web name | Remark | Byte Index | Content | Comment
|  | 1 | Pump Speed Max | Pump Speed Max | Unit: RPM Format: uint32 Range: 0 ~ 99999
|  | 5 | Pump Speed Min | Pump Speed Min
|  | 9 | Fan Speed Max | Fan Speed Max
|  | 13 | Fan Speed Min | Fan Speed Min
| Query (0xE4) | Auto Control Max/Min Alarm Configuration
|  | Host: |  |  |  | CDU:
| 控制 | Byte Index | Content | Web name | Remark | Byte Index | Content | Comment
|  | 1 | Temperature Command Ratio Range | Temperature Command Ratio Range
|  | 2 | Pressure Command Ratio Range | Pressure Command Ratio Range
|  | 3 | Flow Command Ratio Range | Flow Command Ratio Range

## 詢問頻率
|  | 詢問頻率 | 有在insye列表 | Insyde有在polling 內
Query (0xF3) | Firmware Version Information | 一次即可 | 有(A)(B) | 一次
Query (0x10) | Pressure Sensors Information | 高頻率 | 有(a) | 多
Query (0x11) | Temperature Sensors Information | 高頻率 | 有(b) | 多
Query (0x12) | Flow Sensors Information | 高頻率 | 有(c) | 多
Query (0x13) | Valve Gate Information | 高頻率 | 有(d) | 多
Query (0x14) | Leakage Sensors State Information | 低頻率 | 有(e) | 多
Query (0x15) | Leakage Sensors ADC Value | 這個不需要 | 有(f) (我們不須) | 沒
Query (0x16) | Level Sensors Information | 低頻率 | 有(g) | 多
Query (0x17) | Pump LEDs Information | 這個不需要 | 有(h)(我們不須) | 沒
Query (0x18) | Pumps Information | 高頻率 | 有(i) | 多
Query (0x19) | FAN Row A / B Information | 高頻率 | 有(j) | 沒
Query (0x1A) | PSUs Information | 低頻率 | 有(k) | 多
Query (0x1B) | FAN Door Information | 高頻率 | 有(l) | 沒
Modify (0x01) | CDU Auto / Manual Mode Set | 使用者下指令時 | 有(n) | 沒
Query (0x02) | CDU Target Command Information | 使用者下指令時 | 有(p) | 一次
Modify (0x03) | FAN Door Auto / Manual Mode Set
Query (0x20) | Error Event Information | 低頻率 | 有(m) | 沒
Query (0x50) | Entry Bootloader Command | 預留 | 預留 | 預留
Query (0xE0) | Pressure Sensors Max/Min Alarm Configuration | 預留 | 預留 | 預留
Query (0xE1) | Temperature Sensors Max/Min Alarm Configuration | 預留 | 預留 | 預留
Query (0xE2) | Flow Sensors Max/Min Alarm Configuration | 預留 | 預留 | 預留
Query (0xE3) | Pumps/FANs Speed Max/Min Alarm Configuration | 預留 | 預留 | 預留
Query (0xE4) | Auto Control Max/Min Alarm Configuration | 預留 | 預留 | 預留

## 方案A新需求
優先權排序整理如下:
連結 | 1. BMC 要將 IP address pass 給 CDU. (需定流程或由 Insyde 自行設計) (這是這次合約內的吧)
連結 | 2. CDU 長時間沒回應時, BMC 要嘗試 reset CDU
連結 | 3.Error Event 部份
連結 | 4.Firmware Version Information
連結 | 5. 記憶上一次使用者輸入的資訊
連結 | 6.可讓使用者輸入Alarm_max, Alarm_min(包含流量，pump，風扇，自動控制模式下設定的alarm)
連結 | 7.一次性config (Max Min) 自動控制，系統，sensor類
連結 | 8.log資料出來的圖表 (要寫細節)
連結 | 9.Firmware Update_去更新我們的韌體
連結 | 10.網頁我們可以指定我們要的單位
連結 | 11.SMTP
連結 | 12.網頁更新頻率(1S)
連結 | 13.可以讓insyde知道是哪個機種? EEPROM
連結 | 14.BMC要告知mcu目前2600的版本為何種機種以及版本號
首頁 | 1. BMC 要將 IP address pass 給 CDU. (需定流程或由 Insyde 自行設計) (這是這次合約內的吧)
首頁 | 2. CDU 長時間沒回應時, BMC 要嘗試 reset CDU
04/11: 只需要在 application state 做
首頁 | 3.Error Event 部份
首頁 | 4.Firmware Version Information
|  | 參照protocol “Application_Command_ID”分頁的Common “0xF2” , “0xF3” |  |  | 連結 |  | 04/11: 在 BMC init, after BMC update CDU complete, after BMC reset CDU 時, 向 CDU 拿取該資訊
首頁 | 5. 記憶上一次使用者輸入的資訊
|  | 按照 protocol “依序的”將目前 BMC 紀錄的數值存到 .csv, 會花較多工時, |  |  | = >不須"依序"只要Sensor都有輪到就可以 |  |  | 04/11: 在 BMC init, after BMC update CDU complete, after BMC reset CDU, user modify 時 restore CDU setting
參照"Redfish_Name"分頁的C欄位，扣除掉一次性項目(Firmware Version Information)
|  | 例如: | Time, Pr_Liq_Return, Pr_Liq_Supply, Pr_Liq_DP, Pr_Primary_In, Pr_Primary_Out, Temp_Air_Temp_In, ,Temp_Air_Temp_Out, Temp_Liq_Return, Temp_Liq_Supply, Temp_MCU, Temp_Pri_In, Temp_Pri_Out, Temp_Flow_Sup, Temp_Pri_Out, Flow_Supply, Flow_Pri_Out, Primary_Valve, Water_Detect_1, Water_Detect_2, Water_Detect_3, Water_Detect_4, Water_Detect_5, Water_Detect_6, Tank_Level, RPM_P1,RPM_P2, RPM_P3, PWM_P1, PWM_P2, PWM_P3, RPM_RowA_F1, RPM_RowA_F1, RPM_RowA_F2, RPM_RowA_F3, RPM_RowA_F4, RPM_RowA_F5, .....,Current_FDoor_E1, Current_FDoor_E2, Current_FDoor_E3, Current_FDoor_E4,Air_Velocity_E, Temp_Air_In_E, Temp_Air_Out_E
10:00:00,400, 200, 150, 300, 200, 50,....,10, 20, 34
首頁 | 6.可讓使用者輸入Alarm_max, Alarm_min(包含流量，pump，風扇，自動控制模式下設定的alarm)
此部分是會從網頁上讓使用者輸入想要設定的Alarm值，把設定的值下給MCU所以，BMC不會去Get
首頁 | 7.一次性config (Max Min) 自動控制，系統，sensor類
|  | 1 | Sensor類參照"Redfish Name"的"Max Value"以及"Min Value" |  | 連結
|  | 2 | Set Configuration (0x01)
|  | 3 | Setting Mode (0xE0),(0xE1), (0xE2), (0xE3), (0xE4)
首頁 | 8.log資料出來的圖表 (要寫細節) |  |  |  | 04/16_insyde: Type 選單是否為各類 sensor? 類似 Temperature, RPM sensor 等等? 依單位區分?
Auras answer: 我們需要可以選擇要顯示圖表上的sensor (可勾選)
| 1. 需要明確指出那哪些, 因就正常來說 Application Version 不會拿來做成圖表 | [5 empty] | 情境: 我們可能想看MCU Temperature，Supply Flow ，以及Supply Pressure 的變化，所以要可勾選
( 若後續提供的 document 有新增新的需要顯示的, 會視為新需求, 並重估工時及 Target Date )
Auras : 是的，這個不會拿來做成圖表，圖表就用你預設的
2. 需就 CSV 內容, 詳細說明欲顯示格式.
| 例如: | Time, Pr_Liq_Return, Pr_Liq_Supply, Pr_Liq_DP, Pr_Primary_In, Pr_Primary_Out, Temp_Air_Temp_In, ,Temp_Air_Temp_Out, Temp_Liq_Return, Temp_Liq_Supply, Temp_MCU, Temp_Pri_In, Temp_Pri_Out, Temp_Flow_Sup, Temp_Pri_Out, Flow_Supply, Flow_Pri_Out, Primary_Valve, Water_Detect_1, Water_Detect_2, Water_Detect_3, Water_Detect_4, Water_Detect_5, Water_Detect_6, Tank_Level, RPM_P1,RPM_P2, RPM_P3, PWM_P1, PWM_P2, PWM_P3, RPM_RowA_F1, RPM_RowA_F1, RPM_RowA_F2, RPM_RowA_F3, RPM_RowA_F4, RPM_RowA_F5, .....,Current_FDoor_E1, Current_FDoor_E2, Current_FDoor_E3, Current_FDoor_E4,Air_Velocity_E, Temp_Air_In_E, Temp_Air_Out_E
10:00:00,400, 200, 150, 300, 200, 50,....,10, 20, 34
此畫面依照Sensor類型去做區分，但使用者可勾選想要的項目
首頁 | 9.Firmware Update_去更新我們的韌體 |  |  |  | 04/11: 只需參照目前 Excel 流程做即可, 額外的錯誤處理待之後視為新需求來做
| 根據"CDU_Bootloader_Command_ID"分頁進行做動即可 |  |  | 連結
首頁 | 10.網頁我們可以指定我們要的單位 | [8 empty] | 溫度 | 壓力 | 流量
[9 empty] | protocol單位 | °C | kPa | L/s
[9 empty] | 網頁單位 | °C | kPa | LPM=L/s×60
[10 empty] | °F=(°C×59​)+32 | psi=kPa×0.145038 | GPM(美規的)=L/s×15.8503
此選項是由控制頁面有下拉選單 選擇單位，網頁的Sensor readings以及需求五的圖表的單位都要跟著變化
首頁 | 11.SMTP
此項目已包含在Insyde既有的系統內了
首頁 | 12.網頁更新頻率(1S)
首頁 | 13.可以讓insyde知道是哪個機種? EEPROM
此功能先進行按照FRU的格式進行，機種判定格式資料候補
首頁 | 14.BMC要告知mcu目前2600的版本為何種機種以及版本號