## 工作表1
主標題 | 副標題 | AST2600 Hardware Abstraction Layer (HAL) table | [6 empty] | 備註 (計算公式) | LCM畫面
|  | Funtion | Unit | Max Value | Min Value | Device | HAL | Redfish API
1. Liquid (Secondary Temp. ) | Inlet | Temp. (PT-100) | °C | 115 | -40 | PT-100 | struct pt100_device temperature | Sec_Inlet_T |  | LCM為Return Temp.
| Outlet | LIQUID_FLOW1_Temp | °C | 150 | -25 | FXFF101 | struct adc_device temperature1 | Sec_Outlet_T |  | LCM為Supply Temp.
2. Primary Temp. | Inlet | [6 empty] | X
| Outlet | [6 empty] | X
3. Air Flow Temp. | Inlet | [6 empty] | X
| Outlet | [6 empty] | X
4. MCU Temp. |  | CPU Temp sensor | °C | 125 | -55 | PCT2075GV | struct system_board_info temperautre | MCU_T
5. Pressure | Pressure Drop | Pressure1 | kPa | 1600 | -1600 | 42CPT8-10 | insyde進行Outlet - Inlet | Sec_dP
| Pressure inlet | Pressure1 | kPa | 1500 | -1000 | 42CPT8-10 | struct adc_device pressure1 | Sec_Inlet_P
| Pressure outlet | Pressure2 | kPa | 1500 | -1000 | 42CPT8-10 | struct adc_device pressure2 | Sec_Outlet_P
6. Flow Rate |  | LIQUID_FLOW1 | L/s | 4.6 | 0 | FXFF101 | struct adc_device flow1 | Sec_Flow | LPM更改為L/s,數值要除以60(modbus是LPM) | LCM為Flow Rate
7.Pump Status | Pump 1 (Abnormal/ON/OFF) | LED_紅1/LED_綠1 | On/Off | On | Off | LED | struct led_status led1/led4 | P1_LED_R/P1_LED_G
| Pump 1 PWM | PumpPwm1 | strength | 1 | 0.1 | INTG8-484 | struct pump_device lv1 | P1_PWM
| Pump 1 Speed | PumpSpeed1 | RPM | 10000 | 0 | INTG8-484 | struct pump_device speed[0] | P1_Speed
| Pump 1 Temp. | Temperature1(NTC1) | °C | 150 | -40 | NTCALUG01T103G501A | struct adc_device temperature2 | P1_T
| Pump 1 Fan (Abnormal/ON/OFF) | LED_黃1 | On/Off | On | Off | LED | struct led_status led6 | P1_LED_Y
| Pump 1 Fan PWM | FanPwm1 | strength | 1 | 0.1 | DFPK0456B2GY0Q6 | struct fan_device lv1_4 | P1_Fan_PWM
| Pump 1 Fan Speed1 | FanSpeed1 | RPM | 40000 | 0 | DFPK0456B2GY0Q6 | struct fan_device speed[0] | P1_Fan_1_Speed
| Pump 1 Fan Speed2 | FanSpeed2 | RPM | 40000 | 0 | DFPK0456B2GY0Q6 | struct fan_device speed[1] | P1_Fan_2_Speed
| Pump 2 (Abnormal/ON/OFF) | LED_紅2/LED_綠2 | On/Off | On | Off | LED | struct led_status led2/led5 | P2_LED_R/P2_LED_G
| Pump 2 PWM | PumpPwm2 | strength | 1 | 0.1 | INTG8-484 | struct pump_device lv2 | P2_PWM
| Pump 2 Speed | PumpSpeed2 | RPM | 10000 | 0 | INTG8-484 | struct pump_device speed[1] | P2_Speed
| Pump 2 Temp. | Temperature2(NTC2) | °C | 150 | -40 | NTCALUG01T103G501A | struct adc_device temperature3 | P2_T
| Pump 2 Fan (Abnormal/ON/OFF) | LED_黃2 | On/Off | On | Off | LED | struct led_status led7 | P2_LED_Y
| Pump 2 Fan PWM | FanPwm2 | strength | 1 | 0.1 | DFPK0456B2GY0Q6 | struct fan_device lv5_8 | P2_Fan_PWM
| Pump 2 Fan Speed1 | FanSpeed3 | RPM | 40000 | 0 | DFPK0456B2GY0Q6 | struct fan_device speed[2] | P2_Fan_1_Speed
| Pump 2 Fan Speed2 | FanSpeed4 | RPM | 40000 | 0 | DFPK0456B2GY0Q6 | struct fan_device speed[3] | P2_Fan_2_Speed
| Pump 3 (Abnormal/ON/OFF) | [6 empty] | X
| Pump 3 PWM | [6 empty] | X
| Pump 3 Speed | [6 empty] | X
8.Filter Status | Status(Normal/Abnormal) | LED_紅3 | On/Off | On | Off | LED | struct led_status led3 | Filter_LED_R
| Pressure outlet | Pressure3 | kPa | 1500 | -100 | 42CPT8-10 | struct adc_device pressure3 | Filter_Inlet_P
9.Fan | Row A PWM | [6 empty] | X
| Row A Fan1 (Normal/Abnormal) | [6 empty] | X
| Row A Fan1 Speed | [6 empty] | X
| Row A Fan2 (Normal/Abnormal) | [6 empty] | X
| Row A Fan2 Speed | [6 empty] | X
| Row A Fan3 (Normal/Abnormal) | [6 empty] | X
| Row A Fan3 Speed | [6 empty] | X
| Row A Fan4 (Normal/Abnormal) | [6 empty] | X
| Row A Fan4 Speed | [6 empty] | X
| Row A Fan5 (Normal/Abnormal) | [6 empty] | X
| Row A Fan5 Speed | [6 empty] | X
| Row B PWM | [6 empty] | X
| Row B Fan1 (Normal/Abnormal) | [6 empty] | X
| Row B Fan1 Speed | [6 empty] | X
| Row B Fan2 (Normal/Abnormal) | [6 empty] | X
| Row B Fan2 Speed | [6 empty] | X
| Row B Fan3 (Normal/Abnormal) | [6 empty] | X
| Row B Fan3 Speed | [6 empty] | X
| Row B Fan4 (Normal/Abnormal) | [6 empty] | X
| Row B Fan4 Speed | [6 empty] | X
| Row B Fan5 (Normal/Abnormal) | [6 empty] | X
| Row B Fan5 Speed | [6 empty] | X
11.Power Status | Power A Power Status | [6 empty] | X
| Power A Power Consumption | PSU1_Watt | W | 4000 | 0 | PSU | struct psu_device totalWatt | PSU1_power | HAL為W |  | 這部分要教Grad改
| Power A Output Voltage | PSU1_V | V | 55 | 0 | PSU | struct psu_device vol | PSU1_Vout | HAL為mV，故數值要除1000 |  | Godspeep直接call
| Power A Output current | PSU1_V | A | 90 | 0 | PSU | struct psu_device cur | PSU1_Aout | HAL為mV，故數值要除1000
| Power B Power Status | [6 empty] | X
| Power B Power Consumption | PSU1_Watt | W | 4000 | 0 | PSU | struct psu_device totalWatt | PSU2_power | HAL為mW，故數值要除1000
| Power B Output Voltage | PSU1_V | V | 55 | 0 | PSU | struct psu_device vol | PSU2_Vout | HAL為mV，故數值要除1000
| Power B Output current | PSU1_V | A | 90 | 0 | PSU | struct psu_device cur | PSU2_Aout | HAL為mV，故數值要除1000
12.Tank Level |  | Level1 | On/Off | On | Off | MN200 | struct input_gpio lv1 | Tank_Level
13.Proportional Valve | Primary Flow Rate | [6 empty] | X
| Primary Pressure inlet | [6 empty] | X
Fan Door (HRU的風扇) | Power Consumption | W | W | 18000 | 0 | Fanboard | struct psu_device fan_total_watt | Fan16wall_power
| Coolant inlet Temp. | ℃/℉ | °C | 115 | -40 | PT-100 | struct fan_wall_dev_status pt100[0] | HEX_Liquid_In_T
| Coolant outlet Temp. | ℃/℉ | °C | 115 | -40 | PT-100 | struct fan_wall_dev_status pt100[1] | HEX_Liquid_Out_T
| Rack Temp. 1 | ℃/℉
| Rack Temp. 2 | ℃/℉
| Row A Air inlet Temp. | ℃/℉
| Row A Air outlet Temp. | ℃/℉
| Row A Air Temp.1 | % | ℃/℉ | 100℃ | 0 | FanWall05_Board | struct fan_wall_dev_status air_temperature[0] | RowA_Air_T1
| Row A Air Temp.2 | Normal/Err | ℃/℉ | 100℃ | 0 | FanWall05_Board | struct fan_wall_dev_status air_temperature[1] | RowA_Air_T2
| Row A Air Temp.3 | RPM | ℃/℉ |  |  | FanWall05_Board | struct jfan_wall_dev_status air_temperature[2] | RowA_Air_T3 | 紅底為需刪除的
| Row A Air Temp.4 | Normal/Err | ℃/℉ |  |  | FanWall05_Board | struct jfan_wall_dev_status air_temperature[3] | RowA_Air_T4 | 紅底為需刪除的
| Row A Air flow 1 | RPM | CFM |  |  | FanWall05_Board | struct jfan_wall_dev_status air_flow[0] | RowA_Airflow_1 | 紅底為需刪除的
| Row A Air flow 2 | Normal/Err | CFM |  |  | FanWall05_Board | struct jfan_wall_dev_status air_flow[1] | RowA_Airflow_2 | 紅底為需刪除的
| Row A Air flow 3 | RPM | CFM |  |  | FanWall05_Board | struct jfan_wall_dev_status air_flow[2] | RowA_Airflow_3 | 紅底為需刪除的
| Row A Air flow 4 | Normal/Err | CFM |  |  | FanWall05_Board | struct jfan_wall_dev_status air_flow[3] | RowA_Airflow_4 | 紅底為需刪除的
| Row A avg. Air flow | RPM | CFM |  |  | FanWall05_Board |  | RowA_Airflow_AVG
| Row A Air pressure 1 | Normal/Err | kPa | 157 | 0 | FanWall05_Board | struct fan_wall_dev_status air_pressure[0] | RowA_Air_P1
| Row A Air pressure 2 | RPM | kPa | 157 | 0 | FanWall05_Board | struct fan_wall_dev_status air_pressure[1] | RowA_Air_P2
| Row A Air pressure 3 | ℃/℉ | kPa |  |  | FanWall05_Board |  | RowA_Air_P3 | 紅底為需刪除的
| Row A Air pressure 4 | ℃/℉ | kPa |  |  | FanWall05_Board |  | RowA_Air_P4 | 紅底為需刪除的
| Row A avg. Air pressure | % | kPa |  |  | FanWall05_Board |  | RowA_Air_PAVG | 紅底為需刪除的
| Row A PWM | % | % | 100% | 0 | 9GV2048P0G201 | struct fan_wall_dev_ctrl dc[0] | RowA_Fan_PWM
| Row A Fan1 (Normal/Abnormal) | Normal/Err | Normal/Err | 2 | 0 | 9GV2048P0G201 | struct fan_wall_dev_status status[0] | RowA_Fan_1_Check
| Row A Fan1 Speed | RPM | RPM | 60000 | 0 | 9GV2048P0G202 | struct fan_wall_dev_status speed[0] | RowA_Fan_1_Speed
| Row A Fan2 (Normal/Abnormal) | Normal/Err | Normal/Err | 2 | 0 | 9GV2048P0G203 | struct fan_wall_dev_status status[1] | RowA_Fan_2_Check
| Row A Fan2 Speed | RPM | RPM | 60000 | 0 | 9GV2048P0G204 | struct fan_wall_dev_status speed[1] | RowA_Fan_2_Speed
| Row A Fan3 (Normal/Abnormal) | Normal/Err | Normal/Err | 2 | 0 | 9GV2048P0G205 | struct fan_wall_dev_status status[2] | RowA_Fan_3_Check
| Row A Fan3 Speed | RPM | RPM | 60000 | 0 | 9GV2048P0G206 | struct fan_wall_dev_status speed[2] | RowA_Fan_3_Speed
| Row A Fan4 (Normal/Abnormal) | Normal/Err | Normal/Err | 2 | 0 | 9GV2048P0G207 | struct fan_wall_dev_status status[3] | RowA_Fan_4_Check
| Row A Fan4 Speed | RPM | RPM | 60000 | 0 | 9GV2048P0G208 | struct fan_wall_dev_status speed[3] | RowA_Fan_4_Speed
| Row A Fan5 (Normal/Abnormal) | Normal/Err
| Row A Fan5 Speed | RPM
| Row B Air inlet Temp. | ℃/℉
| Row B Air outlet Temp. | ℃/℉
| Row B Air Temp.1 | % | ℃/℉ | 100℃ | 0 | FanWall05_Board | struct fan_wall_dev_status air_temperature[4] | RowB_Air_T1
| Row B Air Temp.2 | RPM | ℃/℉ | 100℃ | 0 | FanWall05_Board | struct fan_wall_dev_status air_temperature[5] | RowB_Air_T2
| Row B Air Temp.3 | RPM | ℃/℉ |  |  | FanWall05_Board | struct jfan_wall_dev_status air_temperature[6] | RowB_Air_T3 | 紅底為需刪除的
| Row B Air Temp.4 | Normal/Err | ℃/℉ |  |  | FanWall05_Board | struct jfan_wall_dev_status air_temperature[7] | RowB_Air_T4 | 紅底為需刪除的
| Row B Air flow 1 | RPM | CFM |  |  | FanWall05_Board | struct jfan_wall_dev_status air_flow[4] | RowB_Airflow_1 | 紅底為需刪除的
| Row B Air flow 2 | Normal/Err | CFM |  |  | FanWall05_Board | struct jfan_wall_dev_status air_flow[5] | RowB_Airflow_2 | 紅底為需刪除的
| Row B Air flow 3 | RPM | CFM |  |  | FanWall05_Board | struct jfan_wall_dev_status air_flow[6] | RowB_Airflow_3 | 紅底為需刪除的
| Row B Air flow 4 | Normal/Err | CFM |  |  | FanWall05_Board | struct jfan_wall_dev_status air_flow[7] | RowB_Airflow_4 | 紅底為需刪除的
| Row B avg. Air flow | RPM | CFM |  |  | FanWall05_Board |  | RowB_Airflow_AVG | 紅底為需刪除的
| Row B Air pressure 1 | Normal/Err | kPa | 157 | 0 | FanWall05_Board | struct fan_wall_dev_status air_pressure[4] | RowB_Air_P1
| Row B Air pressure 2 | RPM | kPa | 157 | 0 | FanWall05_Board | struct fan_wall_dev_status air_pressure[5] | RowB_Air_P2
| Row B Air pressure 3 | ℃/℉ | kPa |  |  | FanWall05_Board |  | RowB_Air_P3 | 紅底為需刪除的
| Row B Air pressure 4 | ℃/℉ | kPa |  |  | FanWall05_Board |  | RowB_Air_P4 | 紅底為需刪除的
| Row B avg. Air pressure | % | kPa |  |  | FanWall05_Board |  | RowB_Air_PAVG | 紅底為需刪除的
| Row B PWM | % | % | 100% | 0 | 9GV2048P0G201 | struct fan_wall_dev_ctrl dc[1] | RowB_Fan_PWM
| Row B Fan1 (Normal/Abnormal) | RPM | Normal/Err | 2 | 0 | 9GV2048P0G201 | struct fan_wall_dev_status status[4] | RowB_Fan_1_Check
| Row B Fan1 Speed | RPM | RPM | 10000 | 0 | 9GV2048P0G202 | struct fan_wall_dev_status speed[4] | RowB_Fan_1_Speed
| Row B Fan2 (Normal/Abnormal) | Normal/Err | Normal/Err | 2 | 0 | 9GV2048P0G203 | struct fan_wall_dev_status status[5] | RowB_Fan_2_Check
| Row B Fan2 Speed | RPM | RPM | 10000 | 0 | 9GV2048P0G204 | struct fan_wall_dev_status speed[5] | RowB_Fan_2_Speed
| Row B Fan3 (Normal/Abnormal) | Normal/Err | Normal/Err | 2 | 0 | 9GV2048P0G205 | struct fan_wall_dev_status status[6] | RowB_Fan_3_Check
| Row B Fan3 Speed | RPM | RPM | 10000 | 0 | 9GV2048P0G206 | struct fan_wall_dev_status speed[6] | RowB_Fan_3_Speed
| Row B Fan4 (Normal/Abnormal) | Normal/Err | Normal/Err | 2 | 0 | 9GV2048P0G207 | struct fan_wall_dev_status status[7] | RowB_Fan_4_Check
| Row B Fan4 Speed | RPM | RPM | 10000 | 0 | 9GV2048P0G208 | struct fan_wall_dev_status speed[7] | RowB_Fan_4_Speed
| Row B Fan5 (Normal/Abnormal) | Normal/Err
| Row B Fan5 Speed | RPM
| Row C Air Temp.1 | % | ℃/℉ | 100℃ | 0 | FanWall05_Board | struct fan_wall_dev_status air_temperature[8] | RowC_Air_T1
| Row C Air Temp 2 | RPM | ℃/℉ | 100℃ | 0 | FanWall05_Board | struct fan_wall_dev_status air_temperature[9] | RowC_Air_T2
| Row C Air Temp 3 | RPM | ℃/℉ |  |  | FanWall05_Board | struct jfan_wall_dev_status air_temperature[10] | RowC_Air_T3 | 紅底為需刪除的
| Row C Air Temp 4 | Normal/Err | ℃/℉ |  |  | FanWall05_Board | struct jfan_wall_dev_status air_temperature[11] | RowC_Air_T4 | 紅底為需刪除的
| Row C Air flow 1 | RPM | CFM |  |  | FanWall05_Board | struct jfan_wall_dev_status air_flow[8] | RowC_Airflow_1 | 紅底為需刪除的
| Row C Air flow 2 | Normal/Err | CFM |  |  | FanWall05_Board | struct jfan_wall_dev_status air_flow[9] | RowC_Airflow_2 | 紅底為需刪除的
| Row C Air flow 3 | RPM | CFM |  |  | FanWall05_Board | struct jfan_wall_dev_status air_flow[10] | RowC_Airflow_3 | 紅底為需刪除的
| Row C Air flow 4 | Normal/Err | CFM |  |  | FanWall05_Board | struct jfan_wall_dev_status air_flow[11] | RowC_Airflow_4 | 紅底為需刪除的
| Row C avg. Air flow | RPM | CFM |  |  | FanWall05_Board |  | RowC_Airflow_AVG | 紅底為需刪除的
| Row C Air pressure 1 | Normal/Err | kPa | 157 | 0 | FanWall05_Board | struct fan_wall_dev_status air_pressure[8] | RowC_Air_P1
| Row C Air pressure 2 | RPM | KPa | 157 | 0 | FanWall05_Board | struct fan_wall_dev_status air pressure[9] | RowC_Air_P2
| Row C Air pressure 3 | ℃/℉ | kPa |  |  | FanWall05_Board |  | RowC_Air_P3 | 紅底為需刪除的
| Row C Air pressure 4 | ℃/℉ | kPa |  |  | FanWall05_Board |  | RowC_Air_P4 | 紅底為需刪除的
| Row C avg. Air pressure | % | kPa |  |  | FanWall05_Board |  | RowC_Air_PAVG | 紅底為需刪除的
| Row C PWM | % | % | 100% | 0 | 9GV2048P0G201 | struct fan_wall_dev_ctrl dc[2] | RowC_Fan_PWM
| Row C Fan1 (Normal/Abnormal) | RPM | Normal/Err | 2 | 0 | 9GV2048P0G201 | struct fan_wall_dev_status status[8] | RowC_Fan_1_Check
| Row C Fan1 Speed | RPM | RPM | 10000 | 0 | 9GV2048P0G202 | struct fan_wall_dev_status speed[8] | RowC_Fan_1_Speed
| Row C Fan2 (Normal/Abnormal) | Normal/Err | Normal/Err | 2 | 0 | 9GV2048P0G203 | struct fan_wall_dev_status status[9] | RowC_Fan_2_Check
| Row C Fan2 Speed | RPM | RPM | 0 | 0 | 9GV2048P0G204 | struct fan_wall_dev_status speed[9] | RowC_Fan_2_Speed
| Row C Fan3 (Normal/Abnormal) | Normal/Err | Normal/Err | 2 | 0 | 9GV2048P0G205 | struct fan_wall_dev_status status[10] | RowC_Fan_3_Check
| Row C Fan3 Speed | RPM | RPM | 10000 | 0 | 9GV2048P0G206 | struct fan_wall_dev_status speed[10] | RowC_Fan_3_Speed
| Row C Fan4 (Normal/Abnormal) | Normal/Err | Normal/Err | 2 | 0 | 9GV2048P0G207 | struct fan_wall_dev_status status[11] | RowC_Fan_4_Check
| Row C Fan4 Speed | RPM | RPM | 10000 | 0 | 9GV2048P0G208 | struct fan_wall_dev_status speed[11] | RowC_Fan_4_Speed
| Row D Air Temp.1 | Normal/Err | ℃/℉ | 100℃ | 0 | FanWall05_Board | struct fan_wall_dev_status air_temperature[12] | RowD_Air_T1
| Row D Air Temp.2 | RPM | ℃/℉ | 100℃ | 0 | FanWall05_Board | struct fan_wall_dev_status air_temperature[13] | RowD_Air_T2
| Row D Air Temp.3 | ℃/℉ | ℃/℉ |  |  | FanWall05_Board | struct jfan_wall_dev_status air_temperature[14] | RowD_Air_T3 | 紅底為需刪除的
| Row D Air Temp.4 | ℃/℉ | ℃/℉ |  |  | FanWall05_Board | struct jfan_wall_dev_status air_temperature[15] | RowD_Air_T4 | 紅底為需刪除的
| Row D Air flow 1 | % | CFM |  |  | FanWall05_Board | struct jfan_wall_dev_status air_flow[12] | RowD_Airflow_1 | 紅底為需刪除的
| Row D Air flow 2 | Normal/Err | CFM |  |  | FanWall05_Board | struct jfan_wall_dev_status air_flow[13] | RowD_Airflow_2 | 紅底為需刪除的
| Row D Air flow 3 | RPM | CFM |  |  | FanWall05_Board | struct jfan_wall_dev_status air_flow[14] | RowD_Airflow_3 | 紅底為需刪除的
| Row D Air flow 4 | Normal/Err | CFM |  |  | FanWall05_Board | struct jfan_wall_dev_status air_flow[15] | RowD_Airflow_4 | 紅底為需刪除的
| Row D avg. Air flow | RPM | CFM |  |  | FanWall05_Board |  | RowD_Airflow_AVG | 紅底為需刪除的
| Row D Air pressure 1 | % | kPa | 157 | 0 | FanWall05_Board | struct fan_wall_dev_status air_pressure[12] | RowD_Air_P1
| Row D Air pressure 2 | RPM | kPa | 157 | 0 | FanWall05_Board | struct fan_wall_dev_status air pressure[13] | RowD_Air_P2
| Row D Air pressure 3 | RPM | kPa |  |  | FanWall05_Board |  | RowD_Air_P3 | 紅底為需刪除的
| Row D Air pressure 4 | Normal/Err | kPa |  |  | FanWall05_Board |  | RowD_Air_P4 | 紅底為需刪除的
| Row D avg. Air pressure | RPM | kPa |  |  | FanWall05_Board |  | RowD_Air_PAVG | 紅底為需刪除的
| Row D PWM | Normal/Err | % | 100% | 0 | 9GV2048P0G201 | struct fan_wall_dev_ctrl dc[3] | RowD_Fan_PWM
| Row D Fan1 (Normal/Abnormal) | RPM | RPM | 2 | 0 | 9GV2048P0G201 | struct fan_wall_dev_status status[12] | RowD_Fan_1_Check
| Row D Fan1 Speed | ℃/℉ | RPM | 10000 | 0 | 9GV2048P0G202 | struct fan_wall_dev_status speed[12] | RowD_Fan_1_Speed
| Row D Fan2 (Normal/Abnormal) | ℃/℉ | Normal/Err | 2 | 0 | 9GV2048P0G203 | struct fan_wall_dev_status status[13] | RowD_Fan_2_Check
| Row D Fan2 Speed | % | RPM | 10000 | 0 | 9GV2048P0G204 | struct fan_wall_dev_status speed[13] | RowD_Fan_2_Speed
| Row D Fan3 (Normal/Abnormal) | Normal/Err | Normal/Err | 2 | 0 | 9GV2048P0G205 | struct fan_wall_dev_status status[14] | RowD_Fan_3_Check
| Row D Fan3 Speed | RPM | RPM | 10000 | 0 | 9GV2048P0G206 | struct fan_wall_dev_status speed[14] | RowD_Fan_3_Speed
| Row D Fan4 (Normal/Abnormal) | Normal/Err | Normal/Err | 2 | 0 | 9GV2048P0G207 | struct fan_wall_dev_status status[15] | RowD_Fan_4_Check
| Row D Fan4 Speed | RPM | RPM | 10000 | 0 | 9GV2048P0G208 | struct fan_wall_dev_status speed[15] | RowD_Fan_4_Speed
Insyde需新增 | Air Flow |  | cft_i/min | 30494 | 0 | FanWall05_Board | struct fan_wall_dev_status air_flow | Avg_Air_Flow | cft_i/min就是CFM
| Avg. Air Temp. in |  | ℃ | 85 | -20 | FanWall05_Board | struct fan_wall_dev_status avg_air_temp[0] | Avg_Air_temp_in
| Avg. Air Temp. out |  | ℃ | 85 | -20 | FanWall05_Board | struct fan_wall_dev_status avg_air_temp[1] | Avg_Air_temp_out
| Avg. Air Press. in |  | kPa | 157 | 0 | FanWall05_Board | struct fan_wall_dev_status avg_air_press[0] | Avg_Air_press_in
| Avg. Air Press. out |  | kPa | 157 | 0 | FanWall05_Board | struct fan_wall_dev_status avg_air_press[1] | Avg_Air_press_out
| Avg. Air dP |  | kPa | 157 | 0 | FanWall05_Board | struct fan_wall_dev_status avg_air_press_dp | Avg_Air_dP
| Fan Power Voltage |  | V | 55 | 0 |  | struct fan_wall_dev_status fan_power_voltage | Fan_Power_V
| Fan Power Current |  | A | 410 | 0 |  | struct fan_wall_dev_status fan_power_current | Fan_Power_I
| Coolant Capacity_Air |  | W | 2121000 | 0 |  | struct fan_wall_dev_status coolant_capacity_air | Coolant_Cp_Air
| Coolant Capacity_Liquid |  | W | 2705000 | 0 |  | struct fan_wall_dev_status coolant_capacity_liquid | Coolant_Cp_Liq
| Row A Air dP |  | kPa | 157 | 0 | FanWall05_Board | struct fan_wall_dev_status air_dp[0] | RowA_Air_dP
| Row B Air dP |  | kPa | 157 | 0 | FanWall05_Board | struct fan_wall_dev_status air_dp[1] | RowB_Air_dP
| Row C Air dP |  | kPa | 157 | 0 | FanWall05_Board | struct fan_wall_dev_status air_dp[2] | RowC_Air_dP
| Row D Air dP |  | kPa | 157 | 0 | FanWall05_Board | struct fan_wall_dev_status air_dp[3] | RowD_Air_dP
modbus最大值為65535

## B方案驗收規格
HRU
主標題 | 副標題 | AST2600 Hardware Abstraction Layer (HAL) table
|  | Funtion | Unit | Max Value | Min Value | Device | HAL | Redfish API
1. Liquid (Secondary Temp. ) | Inlet | Temp. (PT-100) | °C | 115 | -40 | PT-100 | struct pt100_device temperature | Sec_Inlet_T
| Outlet | LIQUID_FLOW1_Temp | °C | 150 | -25 | FXFF101 | struct adc_device temperature1 | Sec_Outlet_T
4. MCU Temp. |  | CPU Temp sensor | °C | 125 | -55 | PCT2075GV | struct system_board_info temperautre | MCU_T
5. Pressure | Pressure Drop | Pressure1 | kPa | 1600 | -1600 | 42CPT8-10 | insyde進行Outlet - Inlet | Sec_dP
| Pressure inlet | Pressure1 | kPa | 1500 | -1000 | 42CPT8-10 | struct adc_device pressure1 | Sec_Inlet_P
| Pressure outlet | Pressure2 | kPa | 1500 | -1000 | 42CPT8-10 | struct adc_device pressure2 | Sec_Outlet_P
6. Flow Rate |  | LIQUID_FLOW1 | L/s | 4.6 | 0 | FXFF101 | struct adc_device flow1 | Sec_Flow
7.Pump Status | Pump 1 (Abnormal/ON/OFF) | LED_紅1/LED_綠1 | On/Off | On | Off | LED | struct led_status led1/led4 | P1_LED_R/P1_LED_G
| Pump 1 PWM | PumpPwm1 | strength | 1 | 0.1 | INTG8-484 | struct pump_device lv1 | P1_PWM
| Pump 1 Speed | PumpSpeed1 | RPM | 100000 | 0 | INTG8-484 | struct pump_device speed[0] | P1_Speed
| Pump 1 Temp. | Temperature1(NTC1) | °C | 150 | -40 | NTCALUG01T103G501A | struct adc_device temperature1 | P1_T
| Pump 1 Fan (Abnormal/ON/OFF) | LED_黃1 | On/Off | On | Off | LED | struct led_status led6 | P1_LED_Y
| Pump 1 Fan PWM | FanPwm1 | strength | 1 | 0.1 | DFPK0456B2GY0Q6 | struct fan_device lv1_4 | P1_Fan_PWM
| Pump 1 Fan Speed1 | FanSpeed1 | RPM | 100000 | 0 | DFPK0456B2GY0Q6 | struct fan_device speed[0] | P1_Fan_1_Speed
| Pump 1 Fan Speed2 | FanSpeed2 | RPM | 100000 | 0 | DFPK0456B2GY0Q6 | struct fan_device speed[1] | P1_Fan_2_Speed
| Pump 2 (Abnormal/ON/OFF) | LED_紅2/LED_綠2 | On/Off | On | Off | LED | struct led_status led2/led5 | P2_LED_R/P2_LED_G
| Pump 2 PWM | PumpPwm2 | strength | 1 | 0.1 | INTG8-484 | struct pump_device lv2 | P2_PWM
| Pump 2 Speed | PumpSpeed2 | RPM | 100000 | 0 | INTG8-484 | struct pump_device speed[1] | P2_Speed
| Pump 2 Temp. | Temperature2(NTC2) | °C | 150 | -40 | NTCALUG01T103G501A | struct adc_device temperature2 | P2_T
| Pump 2 Fan (Abnormal/ON/OFF) | LED_黃2 | On/Off | On | Off | LED | struct led_status led7 | P2_LED_Y
| Pump 2 Fan PWM | FanPwm2 | strength | 1 | 0.1 | DFPK0456B2GY0Q6 | struct fan_device lv5_8 | P2_Fan_PWM
| Pump 2 Fan Speed1 | FanSpeed3 | RPM | 100000 | 0 | DFPK0456B2GY0Q6 | struct fan_device speed[2] | P2_Fan_1_Speed
| Pump 2 Fan Speed2 | FanSpeed4 | RPM | 100000 | 0 | DFPK0456B2GY0Q6 | struct fan_device speed[3] | P2_Fan_2_Speed
8.Filter Status | Status(Normal/Abnormal) | LED_紅3 | On/Off | On | Off | LED | struct led_status led3 | Filter_LED_R
| Pressure outlet | Pressure3 | kPa | 1500 | -100 | 42CPT8-10 | struct adc_device pressure3 | Filter_Inlet_P
| Power A Power Consumption | PSU1_Watt | W | 4000 | 0 | PSU | struct psu_device totalWatt | PSU1_power
| Power A Output Voltage | PSU1_V | V | 55 | 0 | PSU | struct psu_device vol | PSU1_Vout
| Power A Output current | PSU1_V | A | 90 | 0 | PSU | struct psu_device cur | PSU1_Aout
| Power B Power Consumption | PSU1_Watt | W | 4000 | 0 | PSU | struct psu_device totalWatt | PSU2_power
| Power B Output Voltage | PSU1_V | V | 55 | 0 | PSU | struct psu_device vol | PSU2_Vout
| Power B Output current | PSU1_V | A | 90 | 0 | PSU | struct psu_device cur | PSU2_Aout
12.Tank Level |  | Level1 | On/Off | On | Off | MN200 | struct input_gpio lv1 | Tank_Level
Fan Door (HRU的風扇) | Power Consumption | W | W | 18000 | 0 | Fanboard | struct psu_device fan_total_watt | Fan16wall_power
| Coolant inlet Temp. | ℃/℉ | °C | 115 | -40 | PT-100 | struct fan_wall_dev_status pt100[0] | HEX_Liquid_In_T
| Coolant outlet Temp. | ℃/℉ | °C | 115 | -40 | PT-100 | struct fan_wall_dev_status pt100[1] | HEX_Liquid_Out_T
| Row A Air Temp.1 | % | ℃/℉ | 100℃ | 0 | FanWall05_Board | struct fan_wall_dev_status air_temperature[0] | RowA_Air_T1
| Row A Air Temp.2 | Normal/Err | ℃/℉ | 100℃ | 0 | FanWall05_Board | struct fan_wall_dev_status air_temperature[1] | RowA_Air_T2
| Row A Air pressure 1 | Normal/Err | kPa | 157 | 0 | FanWall05_Board | struct fan_wall_dev_status air_pressure[0] | RowA_Air_P1
| Row A Air pressure 2 | RPM | kPa | 157 | 0 | FanWall05_Board | struct fan_wall_dev_status air_pressure[1] | RowA_Air_P2
| Row A PWM | % | % | 1 | 0 | 9GV2048P0G201 | struct fan_wall_dev_ctrl dc[0] | RowA_Fan_PWM
| Row A Fan1 (Normal/Abnormal) | Normal/Err | Normal/Err | 2 | 0 | 9GV2048P0G201 | struct fan_wall_dev_status status[0] | RowA_Fan_1_Check
| Row A Fan1 Speed | RPM | RPM | 60000 | 0 | 9GV2048P0G202 | struct fan_wall_dev_status speed[0] | RowA_Fan_1_Speed
| Row A Fan2 (Normal/Abnormal) | Normal/Err | Normal/Err | 2 | 0 | 9GV2048P0G203 | struct fan_wall_dev_status status[1] | RowA_Fan_2_Check
| Row A Fan2 Speed | RPM | RPM | 60000 | 0 | 9GV2048P0G204 | struct fan_wall_dev_status speed[1] | RowA_Fan_2_Speed
| Row A Fan3 (Normal/Abnormal) | Normal/Err | Normal/Err | 2 | 0 | 9GV2048P0G205 | struct fan_wall_dev_status status[2] | RowA_Fan_3_Check
| Row A Fan3 Speed | RPM | RPM | 60000 | 0 | 9GV2048P0G206 | struct fan_wall_dev_status speed[2] | RowA_Fan_3_Speed
| Row A Fan4 (Normal/Abnormal) | Normal/Err | Normal/Err | 2 | 0 | 9GV2048P0G207 | struct fan_wall_dev_status status[3] | RowA_Fan_4_Check
| Row A Fan4 Speed | RPM | RPM | 60000 | 0 | 9GV2048P0G208 | struct fan_wall_dev_status speed[3] | RowA_Fan_4_Speed
| Row B Air Temp.1 | % | ℃/℉ | 100℃ | 0 | FanWall05_Board | struct fan_wall_dev_status air_temperature[4] | RowB_Air_T1
| Row B Air Temp.2 | RPM | ℃/℉ | 100℃ | 0 | FanWall05_Board | struct fan_wall_dev_status air_temperature[5] | RowB_Air_T2
| Row B Air pressure 1 | Normal/Err | kPa | 157 | 0 | FanWall05_Board | struct fan_wall_dev_status air_pressure[4] | RowB_Air_P1
| Row B Air pressure 2 | RPM | kPa | 157 | 0 | FanWall05_Board | struct fan_wall_dev_status air_pressure[5] | RowB_Air_P2
| Row B PWM | % | % | 1 | 0 | 9GV2048P0G201 | struct fan_wall_dev_ctrl dc[1] | RowB_Fan_PWM
| Row B Fan1 (Normal/Abnormal) | RPM | Normal/Err | 2 | 0 | 9GV2048P0G201 | struct fan_wall_dev_status status[4] | RowB_Fan_1_Check
| Row B Fan1 Speed | RPM | RPM | 60000 | 0 | 9GV2048P0G202 | struct fan_wall_dev_status speed[4] | RowB_Fan_1_Speed
| Row B Fan2 (Normal/Abnormal) | Normal/Err | Normal/Err | 2 | 0 | 9GV2048P0G203 | struct fan_wall_dev_status status[5] | RowB_Fan_2_Check
| Row B Fan2 Speed | RPM | RPM | 60000 | 0 | 9GV2048P0G204 | struct fan_wall_dev_status speed[5] | RowB_Fan_2_Speed
| Row B Fan3 (Normal/Abnormal) | Normal/Err | Normal/Err | 2 | 0 | 9GV2048P0G205 | struct fan_wall_dev_status status[6] | RowB_Fan_3_Check
| Row B Fan3 Speed | RPM | RPM | 60000 | 0 | 9GV2048P0G206 | struct fan_wall_dev_status speed[6] | RowB_Fan_3_Speed
| Row B Fan4 (Normal/Abnormal) | Normal/Err | Normal/Err | 2 | 0 | 9GV2048P0G207 | struct fan_wall_dev_status status[7] | RowB_Fan_4_Check
| Row B Fan4 Speed | RPM | RPM | 60000 | 0 | 9GV2048P0G208 | struct fan_wall_dev_status speed[7] | RowB_Fan_4_Speed
| Row C Air Temp.1 | % | ℃/℉ | 100℃ | 0 | FanWall05_Board | struct fan_wall_dev_status air_temperature[8] | RowC_Air_T1
| Row C Air Temp 2 | RPM | ℃/℉ | 100℃ | 0 | FanWall05_Board | struct fan_wall_dev_status air_temperature[9] | RowC_Air_T2
| Row C Air pressure 1 | Normal/Err | kPa | 157 | 0 | FanWall05_Board | struct fan_wall_dev_status air_pressure[8] | RowC_Air_P1
| Row C Air pressure 2 | RPM | KPa | 157 | 0 | FanWall05_Board | struct fan_wall_dev_status air pressure[9] | RowC_Air_P2
| Row C PWM | % | % | 1 | 0 | 9GV2048P0G201 | struct fan_wall_dev_ctrl dc[2] | RowC_Fan_PWM
| Row C Fan1 (Normal/Abnormal) | RPM | Normal/Err | 2 | 0 | 9GV2048P0G201 | struct fan_wall_dev_status status[8] | RowC_Fan_1_Check
| Row C Fan1 Speed | RPM | RPM | 60000 | 0 | 9GV2048P0G202 | struct fan_wall_dev_status speed[8] | RowC_Fan_1_Speed
| Row C Fan2 (Normal/Abnormal) | Normal/Err | Normal/Err | 2 | 0 | 9GV2048P0G203 | struct fan_wall_dev_status status[9] | RowC_Fan_2_Check
| Row C Fan2 Speed | RPM | RPM | 60000 | 0 | 9GV2048P0G204 | struct fan_wall_dev_status speed[9] | RowC_Fan_2_Speed
| Row C Fan3 (Normal/Abnormal) | Normal/Err | Normal/Err | 2 | 0 | 9GV2048P0G205 | struct fan_wall_dev_status status[10] | RowC_Fan_3_Check
| Row C Fan3 Speed | RPM | RPM | 60000 | 0 | 9GV2048P0G206 | struct fan_wall_dev_status speed[10] | RowC_Fan_3_Speed
| Row C Fan4 (Normal/Abnormal) | Normal/Err | Normal/Err | 2 | 0 | 9GV2048P0G207 | struct fan_wall_dev_status status[11] | RowC_Fan_4_Check
| Row C Fan4 Speed | RPM | RPM | 60000 | 0 | 9GV2048P0G208 | struct fan_wall_dev_status speed[11] | RowC_Fan_4_Speed
| Row D Air Temp.1 | Normal/Err | ℃/℉ | 100℃ | 0 | FanWall05_Board | struct fan_wall_dev_status air_temperature[12] | RowD_Air_T1
| Row D Air Temp.2 | RPM | ℃/℉ | 100℃ | 0 | FanWall05_Board | struct fan_wall_dev_status air_temperature[13] | RowD_Air_T2
| Row D Air pressure 1 | % | kPa | 157 | 0 | FanWall05_Board | struct fan_wall_dev_status air_pressure[12] | RowD_Air_P1
| Row D Air pressure 2 | RPM | kPa | 157 | 0 | FanWall05_Board | struct fan_wall_dev_status air pressure[13] | RowD_Air_P2
| Row D PWM | Normal/Err | % | 1 | 0 | 9GV2048P0G201 | struct fan_wall_dev_ctrl dc[3] | RowD_Fan_PWM
| Row D Fan1 (Normal/Abnormal) | RPM | RPM | 2 | 0 | 9GV2048P0G201 | struct fan_wall_dev_status status[12] | RowD_Fan_1_Check
| Row D Fan1 Speed | ℃/℉ | RPM | 60000 | 0 | 9GV2048P0G202 | struct fan_wall_dev_status speed[12] | RowD_Fan_1_Speed
| Row D Fan2 (Normal/Abnormal) | ℃/℉ | Normal/Err | 2 | 0 | 9GV2048P0G203 | struct fan_wall_dev_status status[13] | RowD_Fan_2_Check
| Row D Fan2 Speed | % | RPM | 60000 | 0 | 9GV2048P0G204 | struct fan_wall_dev_status speed[13] | RowD_Fan_2_Speed
| Row D Fan3 (Normal/Abnormal) | Normal/Err | Normal/Err | 2 | 0 | 9GV2048P0G205 | struct fan_wall_dev_status status[14] | RowD_Fan_3_Check
| Row D Fan3 Speed | RPM | RPM | 60000 | 0 | 9GV2048P0G206 | struct fan_wall_dev_status speed[14] | RowD_Fan_3_Speed
| Row D Fan4 (Normal/Abnormal) | Normal/Err | Normal/Err | 2 | 0 | 9GV2048P0G207 | struct fan_wall_dev_status status[15] | RowD_Fan_4_Check
| Row D Fan4 Speed | RPM | RPM | 60000 | 0 | 9GV2048P0G208 | struct fan_wall_dev_status speed[15] | RowD_Fan_4_Speed
Insyde需新增 | Air Flow |  | cft_i/min (CFM) | 510 (30494/60) | 0 | FanWall05_Board | struct fan_wall_dev_status air flow | Avg_Air_Flow
| Avg. Air Temp. in |  | ℃ | 85 | -20 | FanWall05_Board | struct fan_wall_dev_status avg_air_temp[0] | Avg_Air_temp_in
| Avg. Air Temp. out |  | ℃ | 85 | -20 | FanWall05_Board | struct fan_wall_dev_status avg_air_temp[1] | Avg_Air_temp_out
| Avg. Air Press. in |  | Pa | 157 | 0 | FanWall05_Board | struct fan_wall_dev_status avg_air_press[0] | Avg_Air_press_in
| Avg. Air Press. out |  | Pa | 157 | 0 | FanWall05_Board | struct fan_wall_dev_status avg_air_press[1] | Avg_Air_press_out
| Avg. Air dP |  | Pa | 157 | 0 | FanWall05_Board | struct fan_wall_dev_status avg_air_press_dp | Avg_Air_dP
| Fan Power Voltage |  | V | 55 | 0 |  | struct fan_wall_dev_status fan_power_voltage | Fan_Power_V
| Fan Power Current |  | A | 410 | 0 |  | struct fan_wall_dev_status fan_power_current | Fan_Power_I
| Coolant Capacity_Air |  | W | 2121000 | 0 |  | struct fan_wall_dev_status coolant_capacity_air | Coolant_Cp_Air
| Coolant Capacity_Liquid |  | W | 2705000 | 0 |  | struct fan_wall_dev_status coolant_capacity_liquid | Coolant_Cp_Liq
| Row A Air dP |  | Pa | 157 | 0 | FanWall05_Board | struct fan_wall_dev_status air_dp[0] | RowA_Air_dP
| Row B Air dP |  | Pa | 157 | 0 | FanWall05_Board | struct fan_wall_dev_status air_dp[1] | RowB_Air_dP
| Row C Air dP |  | Pa | 157 | 0 | FanWall05_Board | struct fan_wall_dev_status air_dp[2] | RowC_Air_dP
| Row D Air dP |  | Pa | 157 | 0 | FanWall05_Board | struct fan_wall_dev_status air_dp[3] | RowD_Air_dP